## 📋 Cover
✈️ ICS Migration Execution Record Migrating the Unmigrateable — Study Notes ¦ [MtU #04]
Phase 3 — Controlled Migration ¦ Cutover Planning, Execution & Sign-Off
PROJECT INFORMATION
Facility / Site Name
Project Lead
Migration Approach
Asset Being Migrated
Old Device
New Device
Planned Change Window
| Linked Risk Matrix | ICS_Risk_Scoring_Matrix_MtU02.xlsx
| Linked Segmentation Doc | ICS_Segmentation_Design_MtU03.xlsx
| Document Version | v1.0
| Classification | CONFIDENTIAL
SHEETS IN THIS WORKBOOK
| 📋 Pre-Migration Checklist | Everything that must be verified complete before the change window opens.
| ✈️ Cutover Run Sheet | Minute-by-minute execution script. Every step, owner, time and Go/No-Go gate.
| 🔬 Staging Test Results | Validation evidence from the staging environment before live execution.
| ↩️ Rollback Plan | Step-by-step rollback procedure if cutover fails or Go/No-Go is not passed.
| 📊 Post-Migration Review | 24-hour and 1-week post-change verification. Formal sign-off record.
| 📖 Reference | Migration approaches, staging guidance and cutover decision framework.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #04] ¦ Free resource — cite with attribution

## 📋 Pre-Migration Checklist
📋 Pre-Migration Checklist ¦ Phase 3 ¦ Every item must be ✅ before change window opens ¦ [MtU #04]
⚠️ This checklist must be fully signed off by the Project Lead and Plant Manager before the change window is authorised to open.
Check ID | Category | Checklist Item | Owner | Evidence / Notes | Status | Verified By | Date Verified
PRE-001 | Technical | New device fully configured and logic validated in staging environment. | OT Engineer | Staging test report ref: STG-001 | ✅ Complete | OT Lead | 2025-03-28
PRE-002 | Technical | Protocol compatibility confirmed — new device communicates with all dependent assets. | OT Engineer | Protocol test log attached | ✅ Complete | OT Lead | 2025-03-28
PRE-003 | Technical | Edge case and alarm behaviour validated in staging (process limits, ESD, manual override). | OT Engineer | Edge case test matrix ref: STG-004 | ✅ Complete | OT Lead | 2025-03-29
PRE-004 | Technical | Old system final configuration backed up and stored securely (offline + off-site copy). | OT Engineer | Backup ref: BAK-2025-03-29 | ✅ Complete | OT Lead | 2025-03-29
PRE-005 | Technical | New device firmware verified against vendor's latest stable release. | OT Engineer | Firmware: v4.1.2 — vendor confirmed stable | ✅ Complete | OT Lead | 2025-03-25
PRE-006 | Technical | Rollback procedure documented, tested in staging and approved. | OT Lead | Rollback plan ref: RBK-001 | ✅ Complete | Plant Manager | 2025-03-30
PRE-007 | Technical | All network rules for new device added to Segmentation Design and Firewall Register. | IT Security | FW rules: FW-009, FW-010 | ✅ Complete | IT Security Lead | 2025-03-27
PRE-008 | Operational | Operators trained on new HMI / interface. Training sign-off sheet completed. | Operations Supervisor | Training records: TRN-2025-03 | ✅ Complete | Ops Supervisor | 2025-03-28
PRE-009 | Operational | Production schedule confirmed — change window falls within lowest-risk period. | Plant Manager | Maintenance window: 2025-04-01 00:00–04:00 | ✅ Complete | Plant Manager | 2025-03-26
PRE-010 | Operational | All key personnel confirmed available for change window (OT engineer, IT security, ops supervisor, safety officer if SIL involved). | OT Lead | Attendance confirmed via email 2025-03-30 | ✅ Complete | OT Lead | 2025-03-30
PRE-011 | Operational | Manual operation procedure available and briefed to operators in case of extended outage. | Operations Supervisor | Manual ops SOP ref: SOP-PRD-007 | ✅ Complete | Ops Supervisor | 2025-03-29
PRE-012 | Operational | Vendor support contact confirmed available during change window (if required). | OT Lead | Siemens support: +XX XXX XXXX — confirmed on standby | ✅ Complete | OT Lead | 2025-03-30
PRE-013 | Change Mgmt | Formal change request raised, reviewed and approved via MOC process. | OT Lead | Change ref: CHG-006 | ✅ Complete | Plant Manager | 2025-03-25
PRE-014 | Change Mgmt | Risk assessment for the migration change completed and signed off. | OT Lead | Risk ref: RSK-MIG-001 | ✅ Complete | Plant Manager | 2025-03-25
PRE-015 | Change Mgmt | Go/No-Go decision authority confirmed — named individual, not committee. | Plant Manager | Go/No-Go authority: Plant Manager [Name] | ✅ Complete | Plant Manager | 2025-03-30
PRE-016 | Change Mgmt | Communications sent to all affected stakeholders — timing, impact, contact during window. | OT Lead | Comms sent 2025-03-28 | ✅ Complete | OT Lead | 2025-03-28
PRE-017 | Safety | Safety impact assessment completed — SIL implications reviewed if applicable. | Safety Engineer | No SIL involvement confirmed for this migration | ✅ Complete | Safety Engineer | 2025-03-27
PRE-018 | Safety | Safety officer briefed and available if any unexpected safety issue arises during window. | Safety Officer | On call during window — contact: [Name] | ✅ Complete | Safety Officer | 2025-03-30
PRE-019 | Safety | Emergency shutdown procedure reviewed — all team members briefed on ESD location and operation. | Safety Officer | ESD briefing completed 2025-03-29 | ✅ Complete | Safety Officer | 2025-03-29
PRE-020 | FINAL GATE | Project Lead sign-off — all items above confirmed ✅. Change window authorised to open. | OT Lead |  | ⏳ Pending
PRE-021 | FINAL GATE | Plant Manager sign-off — migration authorised. | Plant Manager |  | ⏳ Pending

## ✈️ Cutover Run Sheet
✈️ Cutover Run Sheet ¦ Phase 3 ¦ Minute-by-Minute Execution Script ¦ [MtU #04]
⚠️ This is a live execution document. Complete Actual Time and Actual Outcome in real time during the change window. Do not skip steps.
Step ID | Planned Time | Actual Time | Phase | Action / Step | Owner | Expected Outcome | Actual Outcome | Go / No-Go Gate? | Decision | Decision By | Notes / Deviations
RUN-001 | T-48h |  | Pre-Window | Confirm all PRE checklist items ✅. If any item is not complete, do not proceed. | OT Lead | All 21 items ✅ |  | No | — | —
RUN-002 | T-24h |  | Pre-Window | Final briefing with all change window personnel. Walk through run sheet step by step. | OT Lead | All personnel briefed and questions resolved. |  | No | — | —
RUN-003 | T-24h |  | Pre-Window | Confirm vendor support contact is available and briefed (if required). | OT Lead | Vendor standby confirmed. |  | No | — | —
RUN-004 | T-2h |  | Pre-Window | Take final snapshot of old system — configuration export, historian data backup, network traffic baseline. | OT Engineer | Baseline documentation complete. Files stored: BAK-2025-04-01 |  | No | — | —
RUN-005 | T-0:30 |  | Pre-Window | All personnel on site. Confirm communications channel (radio/phone) established. | OT Lead | All team present. Comms verified. |  | No | — | —
RUN-006 | T-0:00 |  | Window Open | Change window officially opens. Record actual start time. | OT Lead | Window open confirmed. |  | No | — | —
RUN-007 | T+0:05 |  | Isolation | Isolate old device from network per VLAN config. Verify process is in safe state / manual hold. | OT Engineer | Old device offline. Process confirmed safe. |  | No | — | —
RUN-008 | T+0:10 |  | Isolation | Confirm dependent assets are holding correctly (no alarms from loss of old device). | Ops Supervisor | Zero unexpected alarms. Process stable. |  | No | — | —
RUN-009 | T+0:15 |  | Commission | Install new device physically. Verify power, connections and indicator status. | OT Engineer | New device powered. Indicators normal. |  | No | — | —
RUN-010 | T+0:20 |  | Commission | Load validated configuration from staging onto new device. | OT Engineer | Configuration loaded. Firmware version confirmed. |  | No | — | —
RUN-011 | T+0:30 |  | Commission | Verify new device communicates with all dependent assets (check protocol handshakes). | OT Engineer | All communication verified: [list assets] |  | No | — | —
RUN-012 | T+0:45 |  | Commission | Run startup sequence. Verify outputs match expected values against staging baseline. | OT Engineer | Outputs within ±2% of staging baseline. |  | No | — | —
RUN-013 | T+1:00 |  | 🚦 GO / NO-GO #1 | DECISION POINT: New device communicating correctly and outputs verified. Safe to transfer process? | OT Lead + Ops Supervisor | GO — proceed to process transfer. NO-GO — execute rollback plan RBK-001. |  | YES — GATE 1 | GO / NO-GO | Plant Manager
RUN-014 | T+1:05 |  | Transfer | Transfer process control to new device. Operator confirms takeover on HMI. | OT Engineer + Ops Supervisor | Process running on new device. Operator confirmed. |  | No | — | —
RUN-015 | T+1:15 |  | Transfer | Monitor process for 15 minutes. Verify all values, alarms, interlocks behaving correctly. | Ops Supervisor | All process values normal. No unexpected alarms. |  | No | — | —
RUN-016 | T+1:30 |  | Transfer | Run through key process scenarios (ramp up, ramp down, alarm test if safe to do so). | OT Engineer + Ops Supervisor | All scenarios passed. Documented in test log. |  | No | — | —
RUN-017 | T+2:00 |  | 🚦 GO / NO-GO #2 | DECISION POINT: Process stable for 45 minutes on new device. Rollback window closing. Confirm GO. | OT Lead + Plant Manager | GO — proceed, rollback window closes. NO-GO — last clean rollback opportunity. |  | YES — GATE 2 | GO / NO-GO | Plant Manager
RUN-018 | T+2:05 |  | Closeout | Remove old device from rack. Label and store for record (do not dispose until post-migration review complete). | OT Engineer | Old device labelled and stored: STORE-OT-001 |  | No | — | —
RUN-019 | T+2:15 |  | Closeout | Update asset inventory — old device status: Decommissioned. New device: Active. | OT Lead | Asset inventory updated: ICS-001 → ICS-001-NEW |  | No | — | —
RUN-020 | T+2:30 |  | Closeout | Update firewall rules and network documentation to reflect new device. | IT Security | Firewall rules FW-009, FW-010 verified active. |  | No | — | —
RUN-021 | T+3:00 |  | Closeout | Change window closes. Final process check — all values normal. | Ops Supervisor | Process confirmed stable. No outstanding issues. |  | No | — | —
RUN-022 | T+3:00 |  | SIGN-OFF | Change window closed. Project Lead and Plant Manager sign-off on successful migration. | OT Lead + Plant Manager | Signed off — migration complete. |  | No | — | —

## 🔬 Staging Test Results
🔬 Staging Test Results ¦ Phase 3 ¦ All Tests Must Pass Before Live Execution ¦ [MtU #04]
Test ID | Test Category | Test Description | Expected Result | Actual Result | Pass / Fail | Tested By | Test Date | Notes / Deviations
STG-001 | Logic Validation | Execute full control logic cycle on new PLC. Compare output values against old PLC baseline. | Outputs within ±1% of old PLC baseline across full cycle. | PASS — outputs matched baseline within 0.3%. No deviations. | ✅ Pass | OT Engineer | 2025-03-25
STG-002 | Logic Validation | Simulate ramp-up sequence from cold start. Verify all interlocks engage in correct sequence. | Interlock sequence matches SOP-PRD-007 exactly. | PASS — interlock sequence correct. Timing within spec. | ✅ Pass | OT Engineer | 2025-03-25
STG-003 | Logic Validation | Simulate ramp-down / shutdown sequence. Verify safe state achieved. | Safe state achieved within 45 seconds per design spec. | PASS — safe state achieved in 38 seconds. | ✅ Pass | OT Engineer | 2025-03-25
STG-004 | Edge Cases | Simulate process high-high alarm condition. Verify ESD response. | ESD triggers within 2 seconds of high-high threshold breach. | PASS — ESD triggered at 1.7 seconds. | ✅ Pass | OT Engineer + Safety | 2025-03-26 | Tested twice. Consistent result.
STG-005 | Edge Cases | Simulate communications loss to field device. Verify failsafe behaviour. | Controller enters fail-safe state and raises alarm within 5 seconds. | PASS — fail-safe state at 4.2 seconds. Alarm raised. | ✅ Pass | OT Engineer | 2025-03-26
STG-006 | Edge Cases | Simulate power cycle. Verify controller recovers to last known state automatically. | Controller restores to last state within 60 seconds of power restore. | PASS — restore in 47 seconds. Last state confirmed. | ✅ Pass | OT Engineer | 2025-03-26
STG-007 | Protocol Compatibility | Verify EtherNet/IP communication with dependent assets (ICS-002, ICS-005, ICS-007). | All three assets confirm successful handshake. Data exchange verified. | PASS — all three assets communicating. Data rates normal. | ✅ Pass | OT Engineer + IT Security | 2025-03-27
STG-008 | Protocol Compatibility | Verify OPC-DA data export to historian simulation. | Historian receives correct tag values at expected polling rate. | PASS — 847 tags confirmed. Polling rate 1 second. | ✅ Pass | OT Engineer | 2025-03-27
STG-009 | HMI / Operator Interface | Operator performs full process control cycle using new HMI. Verify all displays and controls functional. | Operator completes cycle without assistance. All displays correct. | PASS — operator completed cycle. One display label typo corrected. | ✅ Pass | Ops Supervisor | 2025-03-28 | Label correction applied to config. Re-tested and confirmed.
STG-010 | HMI / Operator Interface | Operator locates and responds to simulated alarm on new HMI. | Operator acknowledges alarm within 30 seconds using new interface. | PASS — alarm acknowledged in 18 seconds. | ✅ Pass | Ops Supervisor | 2025-03-28
STG-011 | Rollback Procedure | Execute full rollback procedure in staging. Verify old system can be restored within change window. | Old system restored and operational within 45 minutes. | PASS — old system restored in 32 minutes. All values confirmed. | ✅ Pass | OT Lead | 2025-03-29 | Rollback procedure confirmed viable. Timing well within window.
STG-012 | Security | Verify new device accepts only approved protocols on approved ports. Reject unauthorised connection attempt. | Unauthorised Modbus scan attempt blocked. No response from device. | PASS — scan returned no open ports outside approved list. | ✅ Pass | IT Security | 2025-03-27 | Nozomi sensor confirmed no anomalous traffic during test.

## ↩️ Rollback Plan
↩️ Rollback Plan ¦ Phase 3 ¦ Execute if Go/No-Go Gate is NOT Passed ¦ [MtU #04]
⚠️ Rollback is triggered by NO-GO at either gate in the Cutover Run Sheet. Decision authority: Plant Manager. Do not delay — every minute counts.
Step ID | Planned Time | Actual Time | Action / Step | Owner | Expected Outcome | Actual Outcome | Status | Notes
RBK-001 | T+0:00 (from NO-GO) |  | NO-GO declared by Plant Manager. Record actual time. All team notified immediately. | Plant Manager | NO-GO decision recorded. Team on rollback mode. |  | ⏳ Ready
RBK-002 | T+0:02 |  | Isolate new device from network immediately. Do not attempt further troubleshooting on new device during rollback. | OT Engineer | New device isolated. No network traffic. |  | ⏳ Ready
RBK-003 | T+0:05 |  | Confirm process is in safe state / manual hold. Operations supervisor verifies. | Ops Supervisor | Process confirmed safe. No uncontrolled conditions. |  | ⏳ Ready
RBK-004 | T+0:10 |  | Retrieve old device from staging area (retained per PRE-018). Verify physical condition. | OT Engineer | Old device retrieved. Physical condition confirmed. |  | ⏳ Ready
RBK-005 | T+0:15 |  | Install old device. Load configuration from pre-migration backup (BAK-2025-04-01). | OT Engineer | Old device installed. Backup configuration loaded. |  | ⏳ Ready
RBK-006 | T+0:25 |  | Power old device. Verify communications with all dependent assets. | OT Engineer | All communications restored. Values match pre-change baseline. |  | ⏳ Ready
RBK-007 | T+0:35 |  | Transfer process control back to old device. Operator confirms. | OT Engineer + Ops Supervisor | Process running on old device. Operator confirmed. |  | ⏳ Ready
RBK-008 | T+0:45 |  | Monitor process for 15 minutes. Confirm all values, alarms, interlocks normal. | Ops Supervisor | All process values normal. Process stable. |  | ⏳ Ready
RBK-009 | T+1:00 |  | Restore network rules to pre-change state. Verify with IT Security. | IT Security | Network rules restored. Confirmed by IT Security. |  | ⏳ Ready
RBK-010 | T+1:05 |  | Rollback complete. Plant Manager sign-off. Record actual completion time. | Plant Manager | Rollback signed off. Old system operational. |  | ⏳ Ready
RBK-011 | T+1:10 |  | Raise post-rollback incident record. Document what failed and why. Retain new device for investigation. | OT Lead | Incident record raised: INC-MIG-001 |  | ⏳ Ready
RBK-012 | T+24h |  | Post-rollback review. Root cause analysis of Go/No-Go failure. Define corrective actions before re-attempt. | OT Lead + Plant Manager | Root cause identified. Corrective actions agreed before new change request. |  | ⏳ Ready

## 📊 Post-Migration Review
📊 Post-Migration Review & Sign-Off ¦ Phase 3 ¦ 24-Hour and 1-Week Verification ¦ [MtU #04]
24-HOUR POST-CHANGE REVIEW
| Process stability | All process values confirmed normal at 24-hour mark?
| Alarm review | Any unexpected alarms in first 24 hours? Documented and investigated?
| Performance comparison | New device performance vs. old device baseline — within acceptable range?
| Operator feedback | Any operator concerns with new HMI or interface behaviour?
| Network monitoring | Any anomalous network traffic observed by monitoring tool (Nozomi/Claroty)?
| Historian data | Historian receiving correct data from new device? Data continuity confirmed?
| Outstanding issues | Any issues identified during first 24 hours? Documented with owner and resolution date?
24h Reviewer
24h Review Date
| 24h Outcome | ⏳ Pending
1-WEEK POST-CHANGE REVIEW
| Process stability | Process running stably for full 7 days post-migration?
| Incident review | Any incidents or near-misses in first week linked to migration?
| Compensating controls | Compensating controls for this device removed from register?
| Asset inventory | Asset inventory fully updated — old device decommissioned, new device active?
| Risk register | Risk register updated — asset removed from priority shortlist?
| Documentation | All documentation updated: network diagrams, firewall rules, asset inventory?
| Lessons learned | Lessons learned document completed for project record?
1-Week Reviewer
1-Week Review Date
| 1-Week Outcome | ⏳ Pending
FORMAL SIGN-OFF — MIGRATION COMPLETE
OT Lead sign-off
Plant Manager sign-off
IT Security sign-off
| Safety Engineer sign-off (if SIL involved) | N/A for this migration
Sign-off Date
| Migration Status | ⏳ Pending sign-off

## 📖 Reference
📖 Reference Guide ¦ Migration Approaches, Staging & Cutover Decision Framework
MIGRATION APPROACHES
| Parallel Run | Install new system alongside old. Both run simultaneously receiving same inputs. Compare outputs. Cut over when confident. Best for: PLCs, DCS, SCADA servers where parallel operation is technically feasible.
| Hot Cutover | Old system taken offline during planned maintenance window. New system goes live. Highest risk — requires maximum preparation. Best for: devices where parallel run isn't technically possible due to proprietary protocols or hardware constraints.
| Incremental / Module | Migrate one module, loop, or functional area at a time. Hybrid state during transition. Best for: large DCS environments where full cutover is not feasible. Risk distributed across many small changes.
| Greenfield Alongside | Build entirely new infrastructure. Migrate processes onto it. Decommission old system progressively. Best for: major facility redesigns or systems too compromised for incremental migration. High cost, maximum control.
STAGING ENVIRONMENT ESSENTIALS
| What is staging? | A replica of the target system — same hardware, firmware, configuration and logic — running in a test environment where failures have no operational consequence.
| Why it is non-negotiable | Every hour in staging saves ten in crisis management. The cutover window is for execution, not discovery. If you haven't tested it in staging, you haven't tested it.
| What to test | Logic validation, protocol compatibility, edge cases (alarms, ESD, failsafe), HMI operator workflows, rollback procedure timing. All 12 test categories in the Staging Test Results sheet.
| Operator training | No operator should see the new HMI for the first time during a live cutover. Staging is the training environment. Sign-off required before change window authorised.
GO / NO-GO DECISION FRAMEWORK
| Gate 1 — T+1:00 | New device communicating correctly and outputs verified against baseline. Safe to transfer process? GO: proceed. NO-GO: execute rollback immediately.
| Gate 2 — T+2:00 | Process stable for 45 minutes on new device. Last clean rollback opportunity. After GO at Gate 2, rollback becomes its own complex change. This gate must not be rushed.
| Decision authority | A named individual with clear authority makes the GO/NO-GO call — not a committee. Under time pressure, committee decisions fail. Agree the authority before the window opens.
| NO-GO is not failure | A NO-GO decision and clean rollback is a successful outcome. The failure mode is pressing GO when the system isn't ready. Root cause the NO-GO, fix it, and re-attempt with a new change request.
THE HUMAN ELEMENT
| The veteran engineer | The OT engineer who built and maintained the legacy system for 15 years has knowledge no document captures. Every quirk, every undocumented workaround, every near-miss they absorbed. Involve them from Phase 0. Not as a checkbox — as a genuine contributor.
| Resistance vs. knowledge | Resistance to migration is often not obstruction — it's institutional knowledge trying to surface. When an engineer says 'that won't work,' ask why before overriding them. They may know something the risk matrix doesn't.
| Psychological safety | Team members must feel safe to raise concerns during a change window without fear of being overruled for slowing things down. A team member who goes quiet during a cutover because they don't want to cause a delay is a project risk.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #04] ¦ Template v1.0 ¦ Cite freely with attribution