## 📋 Cover
🔒 ICS Segmentation & Isolation Design Migrating the Unmigrateable — Study Notes ¦ [MtU #03]
Phase 2 — Segmentation & Isolation ¦ NIS2 & IEC 62443 Zone/Conduit Model
PROJECT INFORMATION
Facility / Site Name
Project Lead
Organisation
| Linked Risk Matrix | ICS_Risk_Scoring_Matrix_MtU02.xlsx
| Linked Asset Inventory | ICS_Asset_Inventory_MtU01.xlsx
| Design Version | v1.0
Date Created
Date Last Updated
| Classification | CONFIDENTIAL
SHEETS IN THIS WORKBOOK
| 🔒 Segmentation Design | Target zone architecture, VLAN assignments and firewall placement plan.
| 🚧 Conduit & Firewall Rules | Approved communication paths between zones with protocol and rule specifications.
| 🔑 Remote Access Register | All remote access paths — documented, hardened and decommissioned.
| 📋 Change Management Log | Every network change made during Phase 2 — formal MOC record.
| 🛡️ Compensating Controls | Interim risk reduction measures applied to EOL/unmigratable devices.
| 📖 Reference | Technique guide, NIS2 obligations, IEC 62443 zone model and definitions.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #03] ¦ Free resource — cite with attribution

## 🔒 Segmentation Design
🔒 Segmentation Design ¦ Phase 2 ¦ Target Zone Architecture ¦ [MtU #03]
ZONE IDENTITY | [6 empty] | SECURITY DESIGN |  |  |  |  | COMPLIANCE & STATUS |  | VERIFICATION
Zone ID | Zone Name | VLAN ID | Subnet / IP Range | Purdue Level(s) | Assets Assigned | Asset Count | Security Level (IEC 62443) | Isolation Method | Monitoring Tool | Inbound Rules Summary | Outbound Rules Summary | NIS2 Obligation Met? | Implementation Status | Verified By | Verification Date | Notes
Z-01 | OT Zone 1 | VLAN 10 | 192.168.10.0/24 | 0,1,2 | ICS-001 (PLC), ICS-002 (PLC), ICS-004 (HMI) | 3 | SL-2 | VLAN isolation + OT firewall rule | Nozomi Networks | Allow: Z-01 internal only. Deny: all inbound from IT/corporate. | Allow: historian read-only (OPC-DA port 135) via DMZ firewall only. | Partial | In Progress | OT Lead |  | EOL PLC and Win7 HMI present. Compensating controls sheet for both.
Z-02 | OT Zone 2 | VLAN 20 | 192.168.20.0/24 | 0,1 | ICS-003 (RTU) | 1 | SL-2 | VLAN isolation + decommission undocumented modem | Nozomi Networks | Allow: Z-02 internal only. Deny: all external. | Allow: historian read-only via DMZ only. Deny: all else. | Partial | Urgent — modem active | OT Lead |  | ICS-010 modem physically disconnected 2025-02-01. Zone re-verified post-disconnect.
Z-03 | OT Zone 3 | VLAN 30 | 192.168.40.0/24 | 0,1 | ICS-006 (DCS), ICS-008 (Sensor) | 2 | SL-3 | VLAN isolation + unidirectional gateway to DMZ | Claroty | Allow: SIS internal only. Deny: all inbound. | Allow: historian data export via data diode (read-only, unidirectional). | Yes | Complete | Safety Engineer + OT Lead | 2025-01-15 | SIL 2 zone. Data diode installed. No inbound path to this zone exists.
Z-04 | IT/OT DMZ | VLAN 50 | 192.168.30.0/24 | 2,3 | ICS-005 (EWS), ICS-007 (Historian), ICS-009 (Firewall) | 3 | SL-2 | Dual-firewall DMZ — OT firewall + IT firewall | Claroty + SIEM | Allow: EWS access to PLCs via approved ports only. MFA enforced. | Allow: Historian to corporate BI only. Deny: all direct OT access from corporate. | Partial | In Progress | IT Security + OT Lead |  | Primary IT/OT bridge. Highest monitoring priority. Firewall ruleset audit Q1 2025.
Z-05 | Safety Zone | VLAN 99 | Isolated — no IP | 1 | Safety Instrumented Systems (SIS) | 1 | SL-3 | Physical air-gap + hardwired safety loops | Manual inspection only | No network inbound permitted. | No network outbound permitted. | Yes | Complete | Safety Engineer | 2024-12-01 | Fully air-gapped. Physical access log maintained. Annual SIL verification scheduled.

## 🚧 Conduit & Firewall Rules
🚧 Conduit & Firewall Rule Register ¦ Phase 2 ¦ Approved Communication Paths ¦ [MtU #03]
Rule ID | Source Zone | Source Asset(s) | Destination Zone | Destination Asset(s) | Protocol | Port(s) | Direction | Action | Business Justification | Encrypted? | Authenticated? | Logging Enabled? | Rule Owner | Review Date | Status
FW-001 | OT Zone 1 | ICS-001, ICS-002 | OT Zone 1 | ICS-004 (HMI) | PROFIBUS | N/A | Bidirectional | ALLOW | HMI operator visibility of PLCs required for production. | No | No | Yes | OT Lead | 2025-06-30 | Active
FW-002 | OT Zone 1 | ICS-001, ICS-002 | IT/OT DMZ | ICS-007 (Historian) | OPC-DA | 135 | Outbound only | ALLOW | Process data logging to historian. Read-only. No commands permitted inbound. | No | No | Yes | OT Lead + IT Sec | 2025-04-30 | Active — review OPC-UA migration
FW-003 | IT/OT DMZ | ICS-005 (EWS) | OT Zone 1 | ICS-001 (PLC) | MPI/PROFIBUS | N/A | Bidirectional | ALLOW | Engineering workstation requires PLC programming access during maintenance only. | No | Partial | Yes | OT Lead | 2025-03-31 | Active — MFA enforcement pending
FW-004 | IT/OT DMZ | ICS-007 (Historian) | Corporate IT | BI Systems | TCP | 443 | Outbound only | ALLOW | Business reporting — historian exports KPI data to corporate dashboards. | Yes | Yes | Yes | IT Security | 2025-06-30 | Active
FW-005 | OT Zone 2 | ICS-003 (RTU) | OT Zone 2 | ICS-010 (Modem) | Cellular/PPP | Dynamic | Bidirectional | BLOCK — DECOMMISSION | Undocumented. No business justification. External access path unknown. | No | No | Yes | OT Lead + Management | IMMEDIATE | 🔴 Modem physically disconnected 2025-02-01
FW-006 | Corporate IT | Any | OT Zone 1,2,3 | Any OT Asset | Any | Any | Inbound | DENY ALL | No direct corporate-to-OT access permitted under any circumstances. | N/A | N/A | Yes | IT Security | Permanent | Active — default deny
FW-007 | OT Zone 3 | ICS-006 (DCS) | IT/OT DMZ | ICS-007 (Historian) | OPC-DA (via data diode) | 135 | Outbound only — unidirectional | ALLOW | Safety zone data logging. Unidirectional gateway enforces no inbound path. | No | No | Yes | Safety Engineer | 2025-06-30 | Active — data diode installed
FW-008 | IT/OT DMZ | ICS-005 (EWS) | IT/OT DMZ | ICS-005 (EWS) | RDP | 3389 | Inbound from approved IPs only | ALLOW | Remote engineering access. MFA enforced. IP whitelist: [engineering VPN range only]. | Yes | Yes — MFA | Yes | IT Security | 2025-03-31 | Active — IP restriction applied 2025-01-20

## 🔑 Remote Access Register
🔑 Remote Access Register ¦ Phase 2 ¦ All Access Paths Documented & Hardened ¦ [MtU #03]
Access ID | Access Type | Target Asset(s) | Target Zone | Access Provider | Business Purpose | Documented? | MFA Enforced? | Session Logging? | Jump Server Used? | IP Restriction? | Contract / Expiry | Risk Level | Action Required | Status | Verified By | Verification Date
RA-001 | VPN — Engineer | ICS-005 (EWS) | IT/OT DMZ | Internal IT | Remote engineering access during off-site maintenance. | Yes | Yes — MFA | Yes | Yes | Yes — VPN IP range | Internal — permanent | 🟢 Low | None — fully hardened. Maintain logging review cadence. | Active — Hardened | IT Security | 2025-01-20
RA-002 | 4G Modem — Vendor | ICS-003 (RTU) | OT Zone 2 | Unknown vendor | Unknown — modem undocumented. Found during Phase 0 walkdown. | No | No | No | No | No | Unknown — expired? | 🔴 Critical | PHYSICALLY DISCONNECT. Investigate vendor. Do not reconnect until fully assessed and documented. | 🔴 DISCONNECTED 2025-02-01 | OT Lead | 2025-02-01
RA-003 | RDP — Vendor Support | ICS-004 (HMI) | OT Zone 1 | Siemens Support | Vendor support access for HMI troubleshooting. | Yes | No | Partial | No | No | Contract expires 2025-12-31 | 🟠 High | Enforce MFA immediately. Restrict to Siemens IP range. Enable full session logging. Move to jump server. | In Progress | IT Security + OT
RA-004 | Dial-up Modem — Legacy | ICS-001 (PLC) | OT Zone 1 | Unknown — legacy | Found in documentation review. Physical modem still connected. | Partial | No | No | No | No | Unknown | 🔴 Critical | Physically locate and disconnect. Legacy dial-up creates unmonitored inbound path. | 🔴 Under Investigation | OT Lead
RA-005 | VPN — SCADA Vendor | ICS-007 (Historian) | IT/OT DMZ | OSIsoft / AVEVA | Vendor access for historian maintenance and updates. | Yes | Yes — MFA | Yes | Yes | Yes — vendor IP range | Contract 2026-06-30 | 🟢 Low | None — appropriately controlled. Verify access removed when contract expires. | Active — Hardened | IT Security | 2025-02-15

## 📋 Change Management Log
📋 Change Management Log ¦ Phase 2 ¦ Formal MOC Record — Every Change, Every Time ¦ [MtU #03]
Change ID | Date Raised | Change Type | Asset(s) Affected | Zone(s) Affected | Description of Change | Reason / Justification | Risk if Change Fails | Rollback Plan | Raised By | Approved By | Approval Date | Change Window | Implemented By | Implementation Date | Verification Method | Verified By | Outcome | Linked Firewall Rule
CHG-001 | 2025-01-15 | VLAN Creation | All OT assets | All zones | Created VLAN 10 (OT Zone 1), VLAN 20 (OT Zone 2), VLAN 30 (OT Zone 3), VLAN 50 (DMZ), VLAN 99 (Safety). | Phase 2 segmentation design implementation. Required for zone isolation per IEC 62443. | Incorrect VLAN assignment could isolate production assets and cause process fault. | Revert switch config from backup taken 2025-01-14. OT engineer on standby during change. | OT Lead | Plant Manager + IT Security | 2025-01-10 | 2025-01-15 02:00–04:00 (low production) | OT Lead + Network Engineer | 2025-01-15 | Process verified running normally 30 min post-change. All PLCs communicating. | OT Lead + Ops Supervisor | ✅ Complete — no issues | FW-001, FW-002
CHG-002 | 2025-01-20 | Remote Access Hardening | ICS-005 (EWS) | IT/OT DMZ | Applied IP restriction to RDP on engineering workstation. Restricted to VPN IP range only. | RA-001 hardening — enforce access control on engineering workstation per Phase 1 risk finding. | Engineers unable to connect remotely if VPN IP range incorrect. | Revert firewall rule to previous state. IT Security on call during change. | IT Security | IT Manager | 2025-01-18 | 2025-01-20 18:00–19:00 | IT Security Engineer | 2025-01-20 | Remote VPN test confirmed. Non-VPN access confirmed blocked. Engineer access verified. | IT Security Lead | ✅ Complete — no issues | FW-008
CHG-003 | 2025-02-01 | Decommission — 4G Modem | ICS-010 (Modem), ICS-003 (RTU) | OT Zone 2 | Physical disconnection of undocumented 4G modem from RTU in Substation East. | Critical risk finding from Phase 0. Undocumented external access path. No business justification. | RTU loses any vendor remote access — acceptable as access was undocumented and unjustified. | Modem retained in secure storage pending investigation. RTU verified operational on local network. | OT Lead | Plant Manager | 2025-01-28 | 2025-02-01 06:00–07:00 (shift handover) | OT Lead | 2025-02-01 | RTU confirmed operational. Substation monitoring confirmed via local SCADA. Modem stored securely. | OT Lead + Safety Officer | ✅ Complete — modem secured. Investigation ongoing. | FW-005
CHG-004 | 2025-02-10 | Data Diode Installation | ICS-006 (DCS), ICS-007 (Historian) | OT Zone 3 → IT/OT DMZ | Installed unidirectional gateway (data diode) between OT Zone 3 (Safety Zone) and IT/OT DMZ historian. | SIL 2 zone requires no inbound network path. Data diode enforces physical unidirectionality. | DCS loses historian logging if diode misconfigured — safety system unaffected (hardwired). | Remove data diode and restore direct OPC-DA connection (documented config saved). | Safety Engineer + OT Lead | Plant Manager + Safety Manager | 2025-02-05 | 2025-02-10 00:00–03:00 (planned maintenance window) | Safety Engineer + Network Engineer | 2025-02-10 | Historian receiving data. Inbound path test confirmed blocked. SIL 2 loop verified operational. | Safety Engineer + OT Lead | ✅ Complete — data diode operational | FW-007
CHG-005 | 2025-03-01 | MFA Enforcement — Vendor RDP | ICS-004 (HMI) | OT Zone 1 | Enforcing MFA on Siemens vendor RDP access to HMI. Restricting to Siemens IP range. | RA-003 hardening — vendor access currently has no MFA. High risk on EOL HMI. | Siemens vendor unable to connect if MFA not configured on their end — requires vendor coordination. | Revert to IP-only restriction while MFA reconfigured. IT Security on call. | IT Security | IT Manager + OT Lead | 2025-02-25 | 2025-03-01 10:00–11:00 (coordinated with Siemens) | IT Security + Siemens Engineer |  | MFA test with Siemens engineer. Non-Siemens IP access confirmed blocked. Log review 48hr post. |  | ⏳ Planned | FW-003, RA-003

## 🛡️ Compensating Controls
🛡️ Compensating Controls Register ¦ Phase 2 ¦ Interim Risk Reduction for EOL / Unmigratable Devices ¦ [MtU #03]
Control ID | Asset ID | Asset Name | Zone | Reason Cannot Migrate Yet | Expected Migration Date | Control 1 — VLAN Isolation | Control 2 — Protocol Whitelist | Control 3 — Monitoring | Control 4 — Physical Access | Control 5 — Formal Risk Accept | Risk Acceptance Signed By | Risk Acceptance Date | Review Date | Residual Risk Level | Notes
CC-001 | ICS-001 | PLC-UNIT-01 | OT Zone 1 | EOL hardware. Budget for S7-1500 replacement approved but delivery Q3 2025. | 2025-09-30 | ✅ VLAN 10 — isolated from IT network. Only HMI and historian access permitted. | ✅ Firewall allows PROFIBUS only. All other protocols blocked at zone boundary. | ✅ Nozomi passive monitoring. Alert on any anomalous command patterns. | ✅ Cabinet locked. Access log maintained. Contractor access requires OT Lead approval. | ✅ Risk formally accepted by Plant Manager 2025-01-20. Remediation date committed. | Plant Manager | 2025-01-20 | 2025-06-30 | 🟡 Medium — reduced from 🔴 Critical by compensating controls | Replacement hardware on order. Compensating controls reduce risk to acceptable interim level.
CC-002 | ICS-004 | HMI-CTRL-01 | OT Zone 1 | EOL HMI running Win7. Replacement HMI procurement in progress — delivery Q2 2025. | 2025-05-31 | ✅ VLAN 10 — isolated. No direct network access from corporate or IT. | ✅ Only PROFINET to PLC-UNIT-01 permitted. All other traffic blocked. | ✅ Nozomi monitoring. Physical access audit log reviewed weekly. | ✅ Cabinet locked. Keyboard/mouse removed. Screen-only operation via physical console. | ✅ Risk formally accepted by Plant Manager 2025-01-20. Remediation date committed. | Plant Manager | 2025-01-20 | 2025-04-30 | 🟡 Medium — reduced from 🔴 Critical | Win7 — no patches available. Physical-only access is strongest available interim control.
CC-003 | ICS-003 | RTU-REMOTE-01 | OT Zone 2 | CVE patch requires vendor maintenance window — scheduled Q1 2025. | 2025-03-31 | ✅ VLAN 20 — isolated. 4G modem decommissioned (CHG-003). | ✅ DNP3 and Modbus RTU only. All other protocols denied at zone firewall. | ✅ Nozomi monitoring. DNP3 traffic baselined — alert on deviation. | ✅ Substation physical access restricted. Visitor log maintained. | ✅ Risk accepted by OT Lead 2025-02-01 pending patch window. | OT Lead | 2025-02-01 | 2025-03-31 | 🟡 Medium — reduced from 🟠 High (modem removed) | Patch window confirmed with Schneider for March 2025. Risk significantly reduced post-modem removal.

## 📖 Reference
📖 Reference Guide ¦ Segmentation Techniques, NIS2 Obligations & IEC 62443
SEGMENTATION TECHNIQUES
| VLAN Isolation | Groups assets into separate broadcast domains. Traffic between zones passes through a controlled firewall or conduit. Foundation of the IEC 62443 Zone and Conduit model.
| OT-Aware Firewall | Firewalls that understand industrial protocols (Modbus, DNP3, EtherNet/IP, PROFIBUS). Can enforce deep packet inspection rules specific to ICS communications — e.g. allow read commands, deny write commands.
| Unidirectional Gateway (Data Diode) | Hardware device that physically enforces one-way data flow. Used in highest-criticality environments (SIL 2+, nuclear, water). Data can leave the OT zone; nothing can enter. Eliminates the inbound attack path entirely.
| Remote Access Hardening | Consolidate all remote access through a single audited jump server. Enforce MFA on all sessions. Log every session. Restrict by IP range. Decommission all undocumented or unjustified paths.
| Compensating Controls | Interim risk reduction for devices that cannot be migrated immediately. VLAN isolation + protocol whitelisting + monitoring + physical access control + formal documented risk acceptance with committed remediation date.
NIS2 — WHAT ASSET OWNERS MUST DO NOW
| NIS2 is already in force | The NIS2 Directive came into force across EU member states in October 2024. It is NOT a 2027 problem. If you operate essential services (energy, water, transport, digital infrastructure), you must demonstrate OT security measures NOW.
| Article 21 — Risk Management | NIS2 Article 21 requires organisations to implement technical and organisational measures including network segmentation, access control, and incident detection. Phase 2 of this framework directly addresses these obligations.
| Incident Reporting | NIS2 requires significant incidents to be reported to national authorities within 24 hours (early warning) and 72 hours (full notification). OT incidents affecting essential services qualify.
| Supply Chain Security | NIS2 requires assessment of supplier and vendor security. Every vendor remote access path in your Remote Access Register is a NIS2 supply chain risk item.
| Enforcement | NIS2 penalties for essential entities: up to €10M or 2% of global annual turnover. Management personal liability is also established. This is not a box-ticking exercise.
IEC 62443 — SECURITY LEVELS
| SL-1 | Protection against unintentional or coincidental violations. Basic security hygiene.
| SL-2 | Protection against intentional violation using simple means. Firewall, authentication, basic monitoring. Minimum target for most OT environments.
| SL-3 | Protection against sophisticated attacks with moderate resources. Used for high-criticality processes. Data diodes, advanced monitoring, formal change management.
| SL-4 | Protection against state-level attacks with extensive resources. Nuclear, critical national infrastructure. Rarely required in commercial OT.
MOC — MANAGEMENT OF CHANGE KEY PRINCIPLES
| Document everything | Every change to an OT network must be documented before, during and after. The Change Management Log is your legal and operational record.
| Rollback plan is mandatory | No change proceeds without a tested, documented rollback plan. In OT, if something breaks, you need to restore it in minutes — not hours.
| Verify before and after | Process must be confirmed running normally before the change window closes. Never leave a change unverified.
| Timing matters | Schedule changes during lowest-risk production periods. Never during peak production, shift handover peak, or when key personnel are unavailable.
| Safety systems are separate | Any change near a Safety Instrumented System requires the safety engineer in the room, a full SIL impact assessment, and typically a separate change request.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #03] ¦ Template v1.0 ¦ Cite freely with attribution