## 📋 Cover
✅ ICS Validation & Compliance Evidence Pack Migrating the Unmigrateable — Study Notes ¦ [MtU #05]
Phase 4 — Validate & Document ¦ NIS2 Article 21 & IEC 62443 Audit Evidence
PROJECT INFORMATION
Facility / Site Name
Project Lead
Organisation
Asset(s) Covered
Migration Date
| Linked Documents | MtU #01 Inventory ¦ MtU #02 Risk Matrix ¦ MtU #03 Segmentation ¦ MtU #04 Execution
| Document Version | v1.0
| Classification | CONFIDENTIAL
SHEETS IN THIS WORKBOOK
| ✅ Validation Test Report | Four-layer validation: Functional, Security, Performance, Integration. Signed per asset.
| 📄 Compliance Evidence Summary | One-page audit cover sheet per asset. Maps risk → controls → evidence → standard.
| 🗂️ Updated Asset Register | Decommissioned old devices, activated new. Living inventory maintained.
| 📝 Lessons Learned | What worked, what deviated, what to do differently. Feeds the next migration.
| 🔍 Audit Readiness Checklist | Pre-audit self-assessment mapped to NIS2 Article 21 and IEC 62443 obligations.
| 📖 Reference | Validation layer definitions, NIS2 evidence obligations, IEC 62443 mapping.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #05] ¦ Free resource — cite with attribution

## ✅ Validation Test Report
✅ Validation Test Report ¦ Phase 4 ¦ Four-Layer Evidence ¦ [MtU #05]
Asset: ICS-001 (PLC-UNIT-01 → Siemens S7-1500 replacement) ¦ Migration Date: 2025-04-01 ¦ This report must be signed by OT Lead and Plant Manager before asset is removed from risk register.
Test ID | Layer | Test Description | Acceptance Criteria | Method | Result | Pass / Fail | Reference Document | Tested By | Test Date | Notes
VTR-001 | ① Functional | All control loops operating within specification post-migration. | All loop outputs within ±2% of pre-migration baseline for 24 hours. | Live monitoring — Nozomi + historian tag comparison | All 14 loops confirmed within ±0.8% of baseline. 24-hour monitoring complete. | ✅ Pass | MtU #04 Staging STG-001 | OT Engineer | 2025-04-02
VTR-002 | ① Functional | All alarm conditions trigger correctly on new PLC. | Alarm test matrix — 100% of configured alarms trigger within spec. | Alarm test procedure ATM-001 | 47/47 alarms triggered correctly. Response times within spec. | ✅ Pass | MtU #04 Staging STG-002 | OT Engineer | 2025-04-02
VTR-003 | ① Functional | All interlock sequences execute in correct order and timing. | Interlock sequence matches SOP-PRD-007 exactly. | Manual test — SOP-PRD-007 walkthrough | All 8 interlock sequences confirmed correct. Timing within spec. | ✅ Pass | MtU #04 Staging STG-003 | OT Engineer + Safety | 2025-04-02
VTR-004 | ① Functional | Historian receiving correct tag values from new PLC. | 847 tags confirmed active. Data continuity from migration point. | Historian tag audit — PI System | 847 tags active. No data gaps post-migration. Continuity confirmed. | ✅ Pass | MtU #04 Staging STG-008 | OT Engineer | 2025-04-02
VTR-005 | ① Functional | Operator HMI displaying accurate real-time data. | All HMI displays confirmed accurate against field instrument readings. | Operator walkthrough — 30 key displays verified | All 30 displays confirmed. One display label corrected (non-functional issue). | ✅ Pass | MtU #04 Staging STG-009 | Ops Supervisor | 2025-04-02 | Label correction noted. Config updated.
VTR-006 | ② Security | New PLC firmware is latest stable release. No known CVEs. | Firmware v4.1.2 confirmed. Zero CVEs on cve.mitre.org at validation date. | CVE database check — cve.mitre.org | Firmware v4.1.2 confirmed. CVE search returned zero results for this firmware. | ✅ Pass | Vendor release notes v4.1.2 | IT Security | 2025-04-03 | CVE check to be repeated at 30 days and 90 days post-migration.
VTR-007 | ② Security | Firewall rules correctly applied. Only approved protocols passing. | Only EtherNet/IP (port 44818) and OPC-DA (port 135) permitted. All others blocked. | Passive scan — Nozomi + firewall log review | Scan confirmed only approved ports active. 3 blocked connection attempts logged and reviewed — all benign. | ✅ Pass | MtU #03 FW-001, FW-002 | IT Security | 2025-04-03
VTR-008 | ② Security | New device visible in OT monitoring tool with correct profile. | Device appears in Nozomi with correct IP, MAC, firmware and protocol fingerprint. | Nozomi asset discovery confirmation | Device confirmed in Nozomi. Profile matches design. Baseline behaviour recorded. | ✅ Pass | MtU #03 Segmentation Design Z-01 | IT Security | 2025-04-03
VTR-009 | ② Security | No unauthorised communication paths from new device. | New device communicates only with approved assets per firewall register. | Nozomi traffic analysis — 48 hours post-migration | Zero unauthorised connections detected. All traffic matches approved conduits. | ✅ Pass | MtU #03 FW-001, FW-002, FW-007 | IT Security | 2025-04-04
VTR-010 | ③ Performance | PLC cycle time meets or exceeds old device specification. | Cycle time ≤ 10ms (old device baseline: 8ms average). | Cycle time logging — TIA Portal diagnostics | New device average cycle time: 6.2ms. Improvement of 22% over baseline. | ✅ Pass | Old device benchmark BM-ICS-001 | OT Engineer | 2025-04-03
VTR-011 | ③ Performance | Communication latency within acceptable range. | EtherNet/IP latency ≤ 5ms to all connected assets. | Network latency test — Wireshark capture | Average latency: 2.1ms. Max observed: 3.8ms. All within spec. | ✅ Pass | MtU #03 Network Topology | OT Engineer + IT Security | 2025-04-03
VTR-012 | ③ Performance | Device uptime confirmed for 7-day post-migration period. | Zero unplanned outages in first 7 days. CPU < 80% average. | TIA Portal diagnostics + uptime log | 7-day uptime: 100%. Average CPU: 34%. No anomalies. | ✅ Pass | Cutover sign-off MtU #04 | OT Engineer | 2025-04-08
VTR-013 | ④ Integration | New PLC communicates correctly with HMI-CTRL-01 (ICS-004). | HMI receives all 47 configured tags from new PLC. Display update rate normal. | HMI tag audit — WinCC | 47/47 tags confirmed. Update rate 1 second. All displays correct. | ✅ Pass | MtU #01 Asset Inventory — ICS-004 | OT Engineer | 2025-04-02
VTR-014 | ④ Integration | New PLC communicates correctly with EWS-ENG-01 (ICS-005). | Engineering workstation can connect and read/write PLC logic as designed. | Engineering connection test — TIA Portal | Connection confirmed. Read/write verified. MFA enforced on EWS confirmed. | ✅ Pass | MtU #01 Asset Inventory — ICS-005 | OT Engineer | 2025-04-02
VTR-015 | ④ Integration | New PLC data flows correctly to HIST-01 (ICS-007). | All 847 historian tags receiving data. No gaps since migration point. | PI System tag audit | 847 tags confirmed active. Data continuity verified from 2025-04-01 00:03. | ✅ Pass | MtU #01 Asset Inventory — ICS-007 | OT Engineer | 2025-04-03
VTR-016 | ④ Integration | Safety interlock confirmed — new PLC responds correctly to SIL inputs. | ESD signal from safety system triggers new PLC shutdown within 2 seconds. | ESD integration test — coordinated with Safety Engineer | ESD triggered at T+1.4 seconds. Within spec. Safety Engineer sign-off obtained. | ✅ Pass | MtU #03 Zone Map — Z-05 | OT Engineer + Safety | 2025-04-02 | SIL interaction test documented separately in safety case.
VTR-017 | SIGN-OFF | OT Lead formal validation sign-off. | All 16 tests passed. No open deviations. | Review of complete test record |  | ⏳ Pending | This document | OT Lead
VTR-018 | SIGN-OFF | Plant Manager formal validation sign-off. | OT Lead sign-off obtained. Plant Manager confirms migration complete. | Review of OT Lead sign-off |  | ⏳ Pending | This document | Plant Manager

## 📄 Compliance Evidence Summary
📄 Compliance Evidence Summary ¦ Phase 4 ¦ Audit-Ready Cover Sheet Per Asset ¦ [MtU #05]
ASSET IDENTITY
| Asset ID | ICS-001
| Asset Name | PLC-UNIT-01 → PLC-UNIT-01-NEW
| Old Device | Siemens S7-300 ¦ Firmware V3.3.17 ¦ EOL Dec 2024
| New Device | Siemens S7-1500 ¦ Firmware v4.1.2 ¦ Support Active to 2032
| Migration Date | 2025-04-01
| Process Controlled | Conveyor Line 3 — Production Hall A
RISK TRACEABILITY
| Original Risk Finding | EOL device — CVE-2019-13945 (CVSS 7.8). No patches available. No manual override on controlled process.
| Risk Score (Phase 1) | Composite: 36 — Priority 🟠 High ¦ Vuln: 4 × Consequence: 3 × Exposure: 3
| Risk Matrix Reference | ICS_Risk_Scoring_Matrix_MtU02.xlsx — Row ICS-001
| Compensating Controls | CC-001 — VLAN isolation, protocol whitelist, Nozomi monitoring, physical access control. Applied 2025-01-20.
SECURITY CONTROLS APPLIED (PHASE 2)
| Zone Assignment | OT Zone 1 — VLAN 10 — 192.168.10.0/24
| IEC 62443 Security Level | SL-2 — Protection against intentional violation using simple means.
| Firewall Rules Applied | FW-001 (internal Zone 1 only), FW-002 (historian read-only via DMZ)
| Remote Access | No remote access to this device. Physical access only — cabinet locked.
| Monitoring | Nozomi Networks — device baselined. Alerts configured for anomalous commands.
| Segmentation Reference | ICS_Segmentation_Design_MtU03.xlsx — Zone Z-01, Rules FW-001/FW-002
MIGRATION EVIDENCE (PHASE 3)
| Migration Approach | Hot Cutover — planned maintenance window 2025-04-01 00:00–04:00
| Change Reference | CHG-006 — approved by Plant Manager 2025-03-25
| Pre-Migration Checklist | 21/21 items ✅ — signed off OT Lead + Plant Manager 2025-03-30
| Staging Tests | 12/12 tests ✅ — all passed. Report: ICS_Migration_Execution_Record_MtU04.xlsx
| Go/No-Go Gate 1 | GO — passed at T+1:00. Decision: Plant Manager.
| Go/No-Go Gate 2 | GO — passed at T+2:00. Decision: Plant Manager.
| Rollback | Not required. Migration completed successfully within change window.
| Execution Record | ICS_Migration_Execution_Record_MtU04.xlsx — Cutover Run Sheet
VALIDATION EVIDENCE (PHASE 4)
| Functional Validation | ✅ 5/5 tests passed — loops, alarms, interlocks, historian, HMI confirmed.
| Security Validation | ✅ 4/4 tests passed — firmware clean, firewall rules verified, monitoring confirmed.
| Performance Validation | ✅ 3/3 tests passed — cycle time improved 22%. Latency within spec. 7-day uptime 100%.
| Integration Validation | ✅ 4/4 tests passed — HMI, EWS, historian, safety interlock all confirmed.
| Validation Report Ref | ✅ Validation Test Report — this workbook, sheet: Validation Test Report
| Post-Migration Review | ✅ 24-hour review: no issues. 1-week review: process stable. Sign-off complete.
REGULATORY & STANDARDS MAPPING
| NIS2 Article 21(2)(e) | Network segmentation — demonstrated by Zone Z-01, firewall rules FW-001/FW-002, segmentation design.
| NIS2 Article 21(2)(h) | Asset management — demonstrated by asset inventory MtU #01, this evidence summary.
| NIS2 Article 21(2)(i) | Supply chain security — vendor support contract active. Firmware sourced from Siemens official channel.
| IEC 62443-2-1 | Security management system — risk assessment (MtU #02), change management (MtU #04), validation (this document).
| IEC 62443-3-3 SR 1.1 | Human user identification and authentication — enforced on EWS (MFA), physical access control on PLC cabinet.
| IEC 62443-3-3 SL-2 | Security Level 2 achieved for Zone Z-01. Documented in segmentation design MtU #03.
FORMAL SIGN-OFF
OT Lead
Plant Manager
IT Security Lead
Sign-off Date
| Asset Status | ⏳ Pending sign-off — update to: ✅ Migrated & Validated

## 🗂️ Updated Asset Register
🗂️ Updated Asset Register ¦ Phase 4 ¦ Living Document — Decommissioned & Active ¦ [MtU #05]
Asset ID | Asset Name / Tag | Status | Asset Type | Manufacturer | Model | Firmware Version | Vendor Support | Support Expiry | CVE Status | Zone | Purdue Level | Migration Date | Replaces Asset ID | Validation Report Ref | Last Updated | Notes
ICS-001 | PLC-UNIT-01 | 🔴 Decommissioned | PLC | Siemens | S7-300 | V3.3.17 | EOL | 2024-12-31 | N/A — decommissioned | OT Zone 1 | 1 | 2025-04-01 | — | — | 2025-04-01 | Replaced by ICS-001-NEW. Device retained in secure storage: STORE-OT-001. Do not dispose before 2026-04-01.
ICS-001-NEW | PLC-UNIT-01-NEW | ✅ Active — Validated | PLC | Siemens | S7-1500 CPU 1515 | v4.1.2 | Active | 2032-12-31 | ✅ Clean — checked 2025-04-03 | OT Zone 1 | 1 | 2025-04-01 | ICS-001 | MtU05 VTR — all 16 tests ✅ | 2025-04-08 | Migration complete. 7-day uptime 100%. Next CVE review: 2025-07-03.
ICS-002 | PLC-UNIT-02 | ✅ Active | PLC | Rockwell | ControlLogix L71 | V30.014 | Active | 2030-06-30 | ✅ Clean | OT Zone 1 | 1 | — | — | — | 2025-01-20 | No migration required. Active support. Monitor firmware updates.
ICS-003 | RTU-REMOTE-01 | ✅ Active — Patch Pending | RTU | Schneider | Sepam T40 | V02.06 | Extended | 2026-03-31 | ⚠️ CVE-2022-37300 — patch Q1 2025 | OT Zone 2 | 1 | — | — | — | 2025-02-01 | 4G modem decommissioned. Patch scheduled March 2025. Monitor support expiry.
ICS-004 | HMI-CTRL-01 | ⏳ Migration Planned | HMI | Siemens | WinCC v7.2 | V7.2 SP2 | EOL | 2023-12-31 | 🔴 CVE-2021-37185 | OT Zone 1 | 2 | 2025-05-31 | — | — | 2025-01-20 | Replacement HMI on order. Compensating controls CC-002 active. Migration window: May 2025.
ICS-005 | EWS-ENG-01 | ✅ Active — Hardened | Engineering WS | Dell | OptiPlex 7050 | Win10 LTSC | Active | 2027-10-31 | ✅ Clean | IT/OT DMZ | 2 | — | — | — | 2025-01-20 | MFA enforced. IP restriction applied. RDP access logged.
ICS-006 | DCS-NODE-01 | ✅ Active | DCS Controller | Honeywell | Experion PKS C300 | R501.2 | Active | 2028-12-31 | ✅ Clean | OT Zone 3 | 1 | — | — | — | 2025-01-15 | SIL 2. Data diode installed. MOC required for all changes.
ICS-007 | HIST-01 | ⚠️ Patch Required | Historian | OSIsoft | PI Server 2016 | 3.4.390 | Extended | 2026-06-30 | 🔴 CVE-2023-31409 | IT/OT DMZ | 3 | — | — | — | 2025-01-20 | Patch urgently required. Firewall audit overdue. Priority in next sprint.
ICS-008 | SENSOR-TMP-01 | ✅ Active | Sensor | Endress+Hauser | iTEMP TMT142 | FW 01.04 | Active | 2029-12-31 | ✅ Clean | Field | 0 | — | — | — | 2025-01-15 | Calibration due Q3 2025.
ICS-009 | FIREWALL-OT-01 | ✅ Active | Firewall | Fortinet | FortiGate 100F | 7.2.5 | Active | 2029-12-31 | ✅ Clean | IT/OT DMZ | 2 | — | — | — | 2025-03-01 | Ruleset audit due Q1 2025. IDS signatures updated 2025-03-01.
ICS-010 | MODEM-4G-UNKN | 🔴 Decommissioned | 4G Modem | Sierra Wireless | RV55 | Unknown | UNDOCUMENTED | Unknown | Unknown | OT Zone 2 | 1 | 2025-02-01 | — | — | 2025-02-01 | Physically disconnected 2025-02-01. Stored securely: STORE-OT-002. Investigation ongoing.

## 📝 Lessons Learned
📝 Lessons Learned ¦ Phase 4 ¦ What Worked, What Deviated, What We'd Do Differently ¦ [MtU #05]
LL ID | Category | What Happened | Impact | Root Cause | What We'd Do Differently | Apply To | Owner | Status
LL-001 | Planning | Staging environment setup took 3 weeks — longer than estimated. Delayed overall project by 2 weeks. | Project timeline extended. Change window rescheduled once. | Staging hardware procurement not started early enough. Lead time underestimated. | Start staging hardware procurement in Phase 1, not Phase 2. Build procurement lead time into project plan from day one. | All future migration projects | OT Lead | ✅ Applied to ICS-004 project plan
LL-002 | Technical | Parallel run discovered 3 undocumented PLC behaviours not captured in any documentation. | Would have caused process anomalies post-cutover if not caught. All three resolved before live migration. | Original PLC had been modified in-situ over 15 years. Engineer who made changes had retired. No change records. | Always run parallel where technically feasible. Treat every undocumented behaviour found in parallel as a project success, not a delay. | ICS-004, ICS-006 migrations | OT Engineer | ✅ Added to Phase 3 guidance
LL-003 | People | The veteran OT engineer initially resistant to migration project. Nearly excluded from planning. | Significant risk — engineer had critical knowledge about undocumented behaviours (see LL-002). | Engineer felt their expertise was being sidelined. Early project communications focused on compliance rather than operational continuity. | Involve veteran engineers from Phase 0 as named contributors, not reviewers. Frame the project around operational improvement, not just compliance. | All future projects | Project Lead | ✅ Updated project kickoff template
LL-004 | Change Mgmt | One pre-migration checklist item (PRE-010) was signed off without all key personnel formally confirming availability. | Ops Supervisor was delayed arriving to change window by 20 minutes. No impact — engineer covered — but risk was real. | Availability confirmation was via email chain, not formal individual sign-off. Easy to miss in a busy inbox. | Require individual digital sign-off on attendance confirmation, not just email acknowledgement. Check 48h before window. | All future change windows | OT Lead | ✅ Checklist updated — PRE-010 revised
LL-005 | Security | CVE check on new firmware was done at staging (March) but not repeated at time of live migration (April). | 2-week gap — low risk in this case but a gap in process. New CVEs could theoretically emerge in that window. | Process defined check at staging only. Did not specify repeat check at migration date. | Add mandatory CVE check within 48 hours of migration date to pre-migration checklist. Reference in PRE-005. | Immediately — update all checklists | IT Security | ✅ PRE-005 updated in this workbook
LL-006 | Documentation | Lessons learned document was nearly skipped — project team dispersed before it was completed. | Institutional knowledge nearly lost. Two junior engineers joined the next project without access to these findings. | No formal gate requiring lessons learned completion before project closure. Treated as optional. | Lessons learned completion must be a formal gate before any project is closed. Add to post-migration sign-off sheet as mandatory item. | Immediately — update MtU #04 post-migration review | OT Lead | ✅ Added to Post-Migration Review sign-off

## 🔍 Audit Readiness Checklist
🔍 Audit Readiness Checklist ¦ Phase 4 ¦ NIS2 Article 21 & IEC 62443 Self-Assessment ¦ [MtU #05]
Check ID | Standard / Article | Obligation | Evidence Required | Evidence Location | Status | Gap / Action | Owner | Target Date
ARC-001 | NIS2 Art. 21(2)(a) | Risk analysis and information system security policies. | Documented risk assessment policy. Risk matrix covering OT assets. | ICS_Risk_Scoring_Matrix_MtU02.xlsx — Risk Scoring Matrix | ✅ Complete |  | OT Lead
ARC-002 | NIS2 Art. 21(2)(b) | Incident handling — detection, response, recovery procedures. | Incident response procedure covering OT incidents. Evidence of test or activation. | Incident Response Plan — [ref your IR document] | ⏳ Partial | IR plan exists for IT. OT-specific plan not yet formalised. Draft by Q2 2025. | IT Security + OT Lead | 2025-06-30
ARC-003 | NIS2 Art. 21(2)(c) | Business continuity and crisis management including backups. | Backup procedure for OT configurations. Recovery time objective documented. | Configuration backup procedure — BAK-2025-04-01 (per asset) | ✅ Complete |  | OT Lead
ARC-004 | NIS2 Art. 21(2)(e) | Security in network and information systems acquisition, dev and maintenance. | Documented secure procurement policy. CRA compliance check for new devices. | Vendor Evaluation Checklist — [MtU #06 template] | ⏳ Not Started | MtU #06 template covers this. Formalise procurement policy by Q3 2025. | OT Lead + Procurement | 2025-09-30
ARC-005 | NIS2 Art. 21(2)(e) | Network segmentation controls. | Network segmentation design. Firewall rules. Zone map. | ICS_Segmentation_Design_MtU03.xlsx — all sheets | ✅ Complete |  | IT Security + OT Lead
ARC-006 | NIS2 Art. 21(2)(f) | Policies and procedures to assess effectiveness of cybersecurity risk-management measures. | Validation test reports per migrated asset. Audit readiness checklist. | This workbook — Validation Test Report + this sheet | ✅ Complete |  | OT Lead
ARC-007 | NIS2 Art. 21(2)(h) | Basic cyber hygiene practices and cybersecurity training. | Training records for OT and IT staff. Documented hygiene policy. | Operator training records TRN-2025-03. IT security awareness — [ref] | ⏳ Partial | OT operator training complete. IT/OT security awareness training not yet formalised. | HR + IT Security | 2025-06-30
ARC-008 | NIS2 Art. 21(2)(i) | Supply chain security policies covering suppliers and service providers. | Vendor access register. Supplier security assessments. Contract terms. | ICS_Segmentation_Design_MtU03.xlsx — Remote Access Register | ⏳ Partial | Remote access register complete. Formal supplier security assessment process not yet in place. | OT Lead + Legal | 2025-09-30
ARC-009 | IEC 62443-2-1 | Security management system — policy, organisation, risk assessment. | Documented OT security policy. Risk assessment process. Roles and responsibilities. | Risk matrix MtU #02. Segmentation design MtU #03. Project RACI [MtU #10]. | ⏳ Partial | Policy and risk assessment in place. Formal RACI and OT security policy document pending MtU #10. | OT Lead | 2025-12-31
ARC-010 | IEC 62443-3-3 SL-2 | Zone and conduit model implemented at Security Level 2. | Zone design document. Firewall rules. Evidence of implementation and testing. | ICS_Segmentation_Design_MtU03.xlsx — Segmentation Design + Firewall Rules | ✅ Complete |  | IT Security + OT Lead
ARC-011 | IEC 62443-3-3 SR 7.6 | Network and security configuration settings — documented and maintained. | Network topology map. Firewall rule register. Change management log. | MtU #03 — all sheets. MtU #04 — Change Management Log. | ✅ Complete |  | IT Security
ARC-012 | Cyber Insurance | Evidence of OT asset inventory and risk management for underwriter. | Complete asset inventory. Risk assessment. Segmentation evidence. Migration evidence. | MtU #01 through MtU #05 — full evidence pack | ✅ Complete |  | OT Lead + Finance

## 📖 Reference
📖 Reference ¦ Validation Layers, NIS2 Evidence Obligations & IEC 62443 Mapping
VALIDATION LAYERS
| ① Functional | Does the migrated device do what the old device did, correctly and completely? Control loops, alarms, interlocks, HMI, historian tags — all verified against documented acceptance criteria from staging.
| ② Security | Does the migrated device introduce any new vulnerabilities? Firmware CVE check, firewall rule verification, monitoring tool confirmation, unauthorised traffic check. Compared against Phase 2 Segmentation Design.
| ③ Performance | Is the new device performing at least as well as the old one? Cycle time, communication latency, CPU utilisation, 7-day uptime. Regression from legacy hardware performance is a real risk on modern platforms.
| ④ Integration | Does the migrated device integrate correctly with all dependent assets? Every 'Connected To' relationship from Phase 0 must be verified — not assumed. Integration failures are the most common source of post-migration incidents.
NIS2 ARTICLE 21 — EVIDENCE OBLIGATIONS
| Art. 21(2)(a) | Risk analysis and security policies — your risk matrix (MtU #02) and security policy document.
| Art. 21(2)(b) | Incident handling — OT-specific incident response procedure, tested or activated.
| Art. 21(2)(c) | Business continuity — OT configuration backups, recovery time objectives, tested restoration.
| Art. 21(2)(e) | Network security — segmentation design, firewall rules, zone map, access controls (MtU #03).
| Art. 21(2)(f) | Effectiveness assessment — validation test reports, audit readiness checklist (this workbook).
| Art. 21(2)(i) | Supply chain — vendor remote access register, supplier security assessments, contract terms.
| Penalties | Essential entities: up to €10M or 2% of global annual turnover. Management personal liability established. Board-level awareness is not optional.
THE COMPLIANCE EVIDENCE CHAIN
| Phase 0 → MtU #01 | Asset Inventory — proves you know what's in your environment.
| Phase 1 → MtU #02 | Risk Scoring Matrix — proves you've assessed and prioritised risks systematically.
| Phase 2 → MtU #03 | Segmentation Design — proves risks are being managed with documented controls.
| Phase 3 → MtU #04 | Migration Execution Record — proves changes are made in a controlled, documented way.
| Phase 4 → MtU #05 | Validation & Compliance Evidence — proves the controls work. This is the capstone document.
| Phase 5 → MtU #06 | Operate & Monitor — proves this is ongoing, not a one-time exercise. Coming next.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #05] ¦ Template v1.0 ¦ Cite freely with attribution