## 📋 Instructions
ICS / OT ASSET INVENTORY Phase 0 — Asset Discovery Template
Suitable for SMB → Enterprise ¦ ICS / SCADA / DCS / OT environments
ABOUT THIS TEMPLATE
Purpose | Comprehensive OT/ICS asset inventory for Phase 0 discovery assessments
Scope | Covers all ISA-95 levels: Field devices (L0) through DMZ/Enterprise (L3/L4)
Standards alignment | Aligned to IEC 62443, NIST SP 800-82, CIS Controls v8
Scalability | Works for a single-site SMB or multi-site enterprise — filter/hide unused columns as needed
SHEET GUIDE
📋 Instructions | This sheet — how to use the template
🖥 Asset Register | Primary inventory — one row per physical/logical asset
🌐 Network Map | Network segment & connectivity log
🔓 Vuln Flags | Auto-populated CVE/EOL risk flags from Asset Register
📊 Dashboard | Summary KPIs and charts auto-calculated from register
🔧 Reference Data | Drop-down lists and lookup tables (do not delete)
HOW TO USE
Step 1 — Populate Reference Data | Review the Reference Data sheet. Add your site names, custom asset types, and owners.
Step 2 — Passive monitoring | Connect OT-safe passive monitoring tool (Claroty/Dragos/Nozomi). Export asset list and paste into Asset Register.
Step 3 — Manual walkdown | Walk facility with tablet. Add devices found that passive monitoring missed (serial, air-gapped, legacy).
Step 4 — Documentation review | Cross-reference P&IDs, vendor contracts, old Visio diagrams. Add gaps as new rows.
Step 5 — Review Vuln Flags | Vuln Flags sheet auto-flags EOL, unpatched, and high-CVE devices. Prioritise these for Phase 1.
Step 6 — Dashboard review | Share Dashboard tab with stakeholders for executive summary without exposing raw data.
DATA CLASSIFICATION WARNING
⚠ This document contains sensitive OT asset information. Classify per your organisation's data policy. Recommended minimum: CONFIDENTIAL — RESTRICTED DISTRIBUTION. Do not store on shared drives without access controls.

## 🖥 Asset Register
IDENTITY | [7 empty] | HARDWARE | [7 empty] | LIFECYCLE | [5 empty] | NETWORK | [7 empty] | RISK / VULN |  |  |  |  | OWNERSHIP |  |  |  | PROCESS CONTEXT | [5 empty] | DISCOVERY META
Asset ID | Asset Name / Tag | Asset Type | ISA-95 Level | Site / Facility | Area / Zone | Physical Location | GPS / Grid Ref | Manufacturer | Model / Part No. | Serial Number | Firmware Version | Hardware Revision | OS / Platform | OS Version | CPU / Architecture | Install Date | Last Maintenance | End of Life Date | Vendor Support Status | Warranty Expiry | Asset Criticality | IP Address | MAC Address | Hostname | Network Segment / VLAN | Primary Protocol | Secondary Protocols | Remote Access | Remote Access Method | Known CVEs | CVE Severity (Max) | Patch Status | Last Patch Date | CRA Compliance Status | Asset Owner (OT) | IT Owner / Contact | Vendor / Integrator | Vendor Contract Ref | Process / System | Safety Function | SIL Rating | Impact if Offline | Manual Override Exists | Dependencies | Discovery Method | Discovery Date | Last Verified Date | Verified By | Notes | Attachments / Links
Unique ID — auto-generated or assigned | Friendly name or plant tag | PLC / RTU / HMI / DCS / EWS / Historian / Switch / Firewall / Sensor / Other | 0 = Field, 1 = Controller, 2 = Supervisory, 3 = Site Ops, 4 = Enterprise | Site or facility name | Plant area, control zone, or network segment | Building, room, rack, panel ID | Optional for distributed assets | Device manufacturer | Full model number | Device serial number | Current installed firmware | HW revision if applicable | Windows version, RTOS, embedded OS | Full OS version string | x86, ARM, MIPS, proprietary | Date device was installed | Date of last maintenance or inspection | Vendor published EOL date | Active / Extended / End of Life / Unknown | Warranty expiry date | Critical / High / Medium / Low | Current IP address (if applicable) | MAC address | Device hostname | Segment name or VLAN ID | Modbus, DNP3, PROFINET, EtherNet/IP, IEC 61850, etc. | Additional protocols in use | Yes / No — any remote access method enabled | VPN, RDP, cellular modem, vendor portal, etc. | List CVE IDs if known | Critical / High / Medium / Low / None / Unknown | Up to Date / Patches Available / Cannot Patch / Unknown | Date of last patch or firmware update | In Scope / Compliant / Non-Compliant / Exempt / Unknown | OT engineer or team responsible | IT counterpart if applicable | Vendor or system integrator | Contract or support agreement reference | What physical process does this control? | Yes / No — does this perform a safety function? | SIL 1/2/3/4 if applicable | What happens if this device fails / goes offline? | Yes / No / Partial | Other assets this device depends on (Asset IDs) | Passive / Walkdown / Documentation / Vendor-provided | Date first recorded | Date record was last verified against physical asset | Name of person who verified | Free text notes | Links to diagrams, datasheets, configs
AST-001 | Boiler Feed PLC | PLC | 1 | Site A | Boiler House | BH-Panel-03 |  | Siemens | S7-300 CPU 315-2DP | S7K-21983 | V3.3.17 | HW4 | Windows Embedded | 7 SP1 | x86 | 2012-03-15 | 2023-11-01 | 2023-12-31 | End of Life |  | Critical | 10.10.1.10 | 00:1B:1B:AA:12:34 | BH-PLC-01 | OT-L1-VLAN10 | Modbus TCP | PROFIBUS | No |  | CVE-2019-13945 | High | Patches Available | 2021-06-01 | Non-Compliant | J. Kowalski | IT-OT Ops | Siemens AG | SI-2019-0034 | Controls boiler feed water pumps P-101/102 | No |  | Production halt — manual intervention required | Yes | AST-002,AST-003 | Passive+Walkdown | 2024-01-10 | 2024-01-10 | A. Novak | EOL — migration priority HIGH. No patches since 2021. | P&IDs: BH-001-Rev4
AST-002 | Boiler HMI Station | HMI | 2 | Site A | Boiler House | BH-Control-Room |  | Rockwell | PanelView Plus 7 | PVP-77401 | V10.011 |  | Windows Embedded | CE 6.0 | ARM | 2015-07-20 | 2023-11-01 | 2028-06-30 | Active |  | High | 10.10.2.20 | 00:1B:44:BB:56:78 | BH-HMI-01 | OT-L2-VLAN20 | EtherNet/IP |  | No |  |  | None | Up to Date | 2023-09-15 | Compliant | J. Kowalski | IT-OT Ops | Rockwell Automation | RA-SVC-2022-441 | Operator interface for boiler feed controls | No |  | Operators revert to manual gauges | Yes | AST-001 | Passive | 2024-01-10 | 2024-01-10 | A. Novak | Firmware patched Q3 2023. Next review Q3 2024. | RA FactoryTalk drawings
AST-003 | Water Treatment RTU | RTU | 1 | Site A | Water Treatment | WT-Junction-Box-7 | 51.5074,-0.1278 | ABB | RTU560 | 560-2948-C | R4.1 |  | Proprietary RTOS |  | MIPS | 2008-09-01 | 2022-04-12 | 2026-12-31 | Extended |  | Critical | 192.168.50.5 | 00:AB:CD:EF:11:22 | WT-RTU-07 | OT-L1-VLAN50 | DNP3 | IEC 60870-5-101 | No |  | CVE-2022-30313 | Medium | Cannot Patch |  | Non-Compliant | P. Oliynyk |  | ABB Ltd | ABB-MAINT-EXT-009 | Remote monitoring — water intake flow and pressure | No |  | SCADA loses telemetry; operator dispatched to site | Partial | AST-010 | Passive+Documentation | 2024-01-11 | 2024-01-12 | A. Novak | Cannot patch — vendor states no patch available for this FW branch. Compensating control: network isolation. | DNP3 comms diagram WT-07
AST-004 | SCADA Server Primary | EWS/SCADA | 3 | Site A | Server Room | SR-Rack-A2 |  | Dell | PowerEdge R750 | DLPOW-2021-0049 |  |  | Windows Server | 2019 v1809 | x86-64 | 2021-01-15 | 2024-01-05 | 2031-01-15 | Active | 2027-01-15 | Critical | 10.10.3.100 | 00:DE:AD:BE:EF:01 | SCADA-SRV-01 | OT-L3-VLAN30 | OPC-UA |  | Yes | VPN (site-to-site) |  | None | Up to Date | 2024-01-05 | Compliant | Control Systems Team | IT Infrastructure | Inductive Automation | IA-ENT-2021-001 | Ignition SCADA — site-wide supervisory control | No |  | Full SCADA loss — operators on manual | No | AST-001,AST-002,AST-003 | Documentation | 2024-01-08 | 2024-01-08 | A. Novak | Ignition v8.1.28. Monthly patching cycle in place. Backup server AST-005. | Server room diagram SR-2021
AST-005 | SCADA Historian | Historian | 3 | Site A | Server Room | SR-Rack-A3 |  | OSIsoft | PI Server | PI-OSI-2019-0021 | 2019 SP3 |  | Windows Server | 2016 | x86-64 | 2019-06-01 | 2023-06-01 | 2029-06-01 | Active | 2025-06-01 | High | 10.10.3.101 | 00:DE:AD:BE:EF:02 | PI-SRV-01 | OT-L3-VLAN30 | OPC-DA | SQL | No |  | CVE-2021-33885 | High | Patches Available | 2022-11-01 | Non-Compliant | Control Systems Team | IT Infrastructure | AVEVA (OSIsoft) | PI-SUP-2019-ENT | Process data historian — 5-year retention | No |  | Historical data unavailable; compliance reporting impacted | No | AST-004 | Documentation | 2024-01-08 | 2024-01-08 | A. Novak | Pending PI upgrade to AVEVA PI 2023. CVE patch deferred to upgrade window. | PI architecture doc
AST-006 | Safety PLC — Burner | Safety PLC | 1 | Site A | Boiler House | BH-Safety-Cabinet-1 |  | Hima | HIMax | HX-2017-0033 | V7.0.1 |  | Proprietary SIL OS |  | Proprietary | 2017-03-01 | 2023-11-01 | 2030-03-01 | Active | 2028-03-01 | Critical | 10.10.1.50 | 00:HI:MA:XS:AF:01 | BH-SIS-01 | OT-SIS-VLAN5 | PROFINET |  | No |  |  | None | Up to Date | 2023-11-01 | Compliant | Safety Systems Engineer |  | Hima Paul Hildebrandt | HIMA-SVC-2017-B01 | Burner management system — emergency shutdown | Yes | SIL 2 | ESD triggers automatically; production shutdown | Yes (hardwired) | AST-001 | Walkdown+Documentation | 2024-01-10 | 2024-01-10 | A. Novak | SIL 2 certified. Change management: MOC required for any modification. Last SIL validation: Nov 2023. | SIS SIL certificate 2023
AST-007 | OT Core Switch | Switch | 1 | Site A | Boiler House | BH-Panel-03 |  | Cisco | IE-3400 | FOX2201ABCD | 17.9.3 |  | IOS-XE |  |  | 2020-05-01 | 2023-05-01 | 2030-05-01 | Active |  | High | 10.10.1.1 | 00:CO:CI:SW:01:AA | BH-SW-01 | OT-L1-VLAN10 | Ethernet |  | No |  | CVE-2023-20198 | Critical | Patches Available | 2023-02-01 | Non-Compliant | IT-OT Ops | IT Infrastructure | Cisco | CSCO-SMART-2020-001 | Core switching — boiler house OT network | No |  | Full network outage — boiler house | No |  | Passive | 2024-01-10 | 2024-01-10 | A. Novak | CRITICAL CVE unpatched — maintenance window scheduled Q1 2024. Compensating control: access-lists in place. | Network diagram v2.3
AST-008 | Undocumented Cellular Modem | Remote Access Device | 3 | Site A | Server Room | SR-Rack-B4 |  | Sierra Wireless | RV55 | SWI-2019-9981 | 4.14.0 |  | Embedded Linux |  | ARM | 2019-11-01 |  |  | Unknown |  | Critical | 192.168.99.254 | 00:SW:CE:LL:MO:01 |  | OT-DMZ | TCP/IP |  | Yes | 4G Cellular (undocumented) |  | Unknown | Unknown |  | Non-Compliant | Unknown | Unknown | Sierra Wireless | Unknown | Unknown — discovered during walkdown | No |  | Unknown — not in P&IDs | No |  | Walkdown | 2024-01-11 | 2024-01-11 | A. Novak | ⚠ UNDOCUMENTED DEVICE. Found plugged into rack during physical walkdown. Not in any diagram. Vendor installed 2019 for remote support — never removed. ISOLATE PENDING INVESTIGATION. | Photo: modem-rack-B4.jpg
AST-009 | Flow Transmitter FT-201 | Sensor/Field Device | 0 | Site A | Water Treatment | WT-Line-2 |  | Endress+Hauser | Proline Promag 55 | EH-FT-201-2016 | [5 empty] | 2016-04-01 | 2022-09-01 |  | Active |  | Medium |  |  |  | OT-L0-Serial | HART | 4-20mA | No |  |  | None |  |  | Compliant | Process Team |  | Endress+Hauser | EH-SVC-2016-021 | Water flow measurement — feed line 2 | No |  | Flow data lost; manual sampling required | No | AST-003 | Walkdown | 2024-01-12 | 2024-01-12 | A. Novak | No IP connectivity — HART only. Calibration due 2024-09. | Calibration cert EH-FT201-2023
AST-010 | Engineering Workstation | EWS | 2 | Site A | Engineering Office | EO-Desk-12 |  | HP | EliteDesk 800 G4 | HP-2018-EWS-04 |  |  | Windows | 10 LTSC 2019 | x86-64 | 2018-08-01 | 2023-08-01 | 2029-10-14 | Active | 2024-08-01 | High | 10.10.2.50 | 00:HP:EW:ST:AT:01 | ENG-WS-04 | OT-L2-VLAN20 | EtherNet/IP | USB | No |  |  | Low | Up to Date | 2023-12-01 | Compliant | J. Kowalski | IT-OT Ops | HP / Rockwell |  | PLC programming and configuration workstation | No |  | Engineering changes require physical access | No | AST-001,AST-002 | Passive+Walkdown | 2024-01-10 | 2024-01-10 | A. Novak | USB ports active — policy review required. AV up to date. Connected to OT-L2 only; no IT network access. | Asset sticker photo: EWS-04.jpg

## 🌐 Network Map
NETWORK TOPOLOGY LOG
Segment ID | Segment Name | ISA-95 Level | VLAN ID | IP Subnet | Zone Type | Connected To (Segment ID) | Connection Type | Firewall / ACL Between | Protocol(s) in Use | Remote Access Enabled | Asset Count | Notes
SEG-01 | OT-Field-L0 | 0 | N/A | Serial/4-20mA | Field Zone | SEG-02 | Serial / Analog | None — hardwired | HART, Modbus RTU | No | 12 | Level 0 field instruments. No IP connectivity.
SEG-02 | OT-Controller-L1 | 1 | 10 | 10.10.1.0/24 | Controller Zone | SEG-03 | Ethernet | Purdue Model boundary | Modbus TCP, PROFINET | No | 8 | PLCs, RTUs, safety systems.
SEG-03 | OT-Supervisory-L2 | 2 | 20 | 10.10.2.0/24 | Supervisory Zone | SEG-04 | Ethernet | Managed switch ACL | EtherNet/IP, OPC-DA | No | 5 | HMIs, Engineering Workstations.
SEG-04 | OT-Site-Ops-L3 | 3 | 30 | 10.10.3.0/24 | Site Operations Zone | SEG-05 | Ethernet | Industrial Firewall | OPC-UA, SQL | Yes (VPN) | 4 | SCADA servers, historians. VPN for site-to-site only.
SEG-05 | OT-SIS | 1 | 5 | 10.10.5.0/28 | Safety Instrumented Zone | SEG-02 | Ethernet | Air gap / one-way datadiode | PROFINET | No | 3 | Safety PLC systems. Physically segregated.
SEG-06 | OT-DMZ | 3 | 99 | 192.168.99.0/30 | DMZ | SEG-04,IT-CORP | Ethernet | DMZ firewall both sides | TCP/IP | Unknown | 1 | ⚠ Undocumented modem AST-008 found here. Investigate.

## 🔓 Vuln Flags
VULNERABILITY FLAGS — AUTO-POPULATED
Asset ID | Asset Name | Asset Type | ISA-95 Lvl | Criticality | EOL Flag | CVE Flag | Patch Flag | Remote Access Flag | Undocumented Flag | Risk Score (auto) | Priority | Action Required
ℹ Rows below pull from 🖥 Asset Register. Flags are set: 🔴 = issue found, ✅ = OK, ❓ = unknown. Risk Score 1-10 auto-calculated.
AST-001 | Boiler Feed PLC | PLC | 1 | Critical | 🔴 EOL | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 6 | P2 - HIGH | HIGH: Schedule remediation within 30 days
AST-002 | Boiler HMI Station | HMI | 2 | High | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 3 | P4 - LOW | LOW: Monitor — standard review cycle
AST-003 | Water Treatment RTU | RTU | 1 | Critical | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 5 | P3 - MEDIUM | MEDIUM: Include in migration roadmap
AST-004 | SCADA Server Primary | EWS/SCADA | 3 | Critical | ✅ OK | ❓ Unknown | ❓ Unknown | 🔴 Remote Access | ✅ Documented | 5 | P3 - MEDIUM | MEDIUM: Include in migration roadmap
AST-005 | SCADA Historian | Historian | 3 | High | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 3 | P4 - LOW | LOW: Monitor — standard review cycle
AST-006 | Safety PLC — Burner | Safety PLC | 1 | Critical | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 4 | P3 - MEDIUM | MEDIUM: Include in migration roadmap
AST-007 | OT Core Switch | Switch | 1 | High | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 3 | P4 - LOW | LOW: Monitor — standard review cycle
AST-008 | Undocumented Cellular Modem | Remote Access Device | 3 | Critical | ❓ Unknown | ❓ Unknown | ❓ Unknown | 🔴 Remote Access | ✅ Documented | 5 | P3 - MEDIUM | MEDIUM: Include in migration roadmap
AST-009 | Flow Transmitter FT-201 | Sensor/Field Device | 0 | Medium | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 2 | P4 - LOW | LOW: Monitor — standard review cycle
AST-010 | Engineering Workstation | EWS | 2 | High | ✅ OK | ❓ Unknown | ❓ Unknown | ✅ No Remote | ✅ Documented | 3 | P4 - LOW | LOW: Monitor — standard review cycle

## 📊 Dashboard
ICS ASSET INVENTORY — EXECUTIVE DASHBOARD
Site A ¦ Last updated: 07-Jun-2026
TOTAL ASSETS | CRITICAL ASSETS |  | EOL DEVICES
10 | 5 |  | 1
Unique asset records | Criticality = Critical |  | Vendor support = End of Life
UNPATCHED | REMOTE ACCESS |  | HIGH/CRIT CVEs
0 | 2 |  | 0
Patches available but not applied | Devices with remote access enabled |  | Assets with High or Critical CVEs
ASSET BREAKDOWN BY TYPE
PLC |  | 1
RTU |  | 1
HMI |  | 1
EWS |  | 1
SCADA Server |  | 0
Historian |  | 1
Switch |  | 1
Safety PLC |  | 1
Sensor/Field Device |  | 1
Other |  | 0
CRITICALITY BREAKDOWN
Critical |  | 5
High |  | 4
Medium |  | 1
Low |  | 0

## 🔧 Reference Data
REFERENCE DATA — Drop-down lists and lookup tables. Do not delete or rename this sheet.
ISA-95 PURDUE MODEL LEVELS
Level 0 | Field / Sensor Layer | Sensors, actuators, transmitters, field instruments — physical process
Level 1 | Controller Layer | PLCs, RTUs, Safety PLCs — direct process control
Level 2 | Supervisory Layer | HMIs, Engineering Workstations — supervisory control
Level 3 | Site Operations Layer | SCADA, MES, Historians — site-wide coordination
Level 4 | Enterprise / IT Layer | ERP, business systems — above OT boundary
COMMON OT PROTOCOLS
Modbus RTU/TCP | Schneider, many vendors | Simple, ubiquitous — no auth or encryption
PROFIBUS/PROFINET | Siemens | German standard — industrial automation
EtherNet/IP | Rockwell Automation | CIP over standard Ethernet
DNP3 | Distributed Network Protocol | SCADA/utilities — supports authentication
IEC 60870-5 | IEC Standard | Power systems SCADA
IEC 61850 | IEC Standard | Substation automation — modern
OPC-DA / OPC-UA | OPC Foundation | Interoperability standard; UA = modern, encrypted
HART | FieldComm Group | Field device comms over 4-20mA loops
BACnet | ASHRAE | Building automation and HVAC
Modbus Plus | Schneider | Proprietary extension of Modbus
CRITICALITY SCORING GUIDE
Critical | Direct safety function OR production-critical with no manual backup OR SIL-rated
High | Major production impact if offline; manual backup exists but limited
Medium | Significant operational impact; manual workaround available
Low | Minor impact; easily substituted or redundant
RISK SCORE FORMULA (Vuln Flags sheet)
Component | Points | Notes
Criticality = Critical | +4
Criticality = High | +3
Criticality = Medium | +2
Criticality = Low | +1
Vendor Support = End of Life | +2
Vendor Support = Extended | +1
CVE Severity = Critical or High | +2
CVE Severity = Medium | +1
Patch Status = Cannot Patch | +2
Patch Status = Patches Available | +1
Remote Access = Yes | +1
MAX SCORE | 10 (capped) | Score ≥8 = P1 Critical; ≥6 = P2 High; ≥4 = P3 Medium; <4 = P4 Low