## 📋 Cover
⚖️ ICS Risk Scoring Matrix Migrating the Unmigrateable — Study Notes ¦ [MtU #02]
Phase 1 — Risk Assessment & Prioritisation ¦ IEC 62443 & Consequence-Based Scoring
PROJECT INFORMATION
Facility / Site Name
Assessment Lead
Organisation
| Linked Asset Inventory | ICS_Asset_Inventory_MtU01.xlsx
Date Started
Date Last Updated
| Version | v1.0
| Classification | CONFIDENTIAL
SHEETS IN THIS WORKBOOK
| ⚖️ Risk Scoring Matrix | Score every asset across Vulnerability, Consequence and Exposure. Composite score drives priority tier.
| 🗺️ Zone Map | Group assets into IEC 62443 Security Zones. Identify conduits and lateral movement paths.
| 🏆 Priority Shortlist | Auto-ranked migration shortlist pulled from Risk Matrix. Your project execution order.
| 📖 Reference | Scoring rubrics, consequence scale, zone definitions and standards reference.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #02] ¦ Free resource — cite with attribution

## ⚖️ Risk Scoring Matrix
⚖️ ICS Risk Scoring Matrix ¦ Phase 1 — Risk Assessment & Prioritisation ¦ [MtU #02]
ASSET IDENTITY |  |  |  |  | ① VULNERABILITY (1–5) | [5 empty] | ② CONSEQUENCE (1–5) | [5 empty] | ③ EXPOSURE (1–5) |  |  |  |  | COMPOSITE & ACTION
Asset ID | Asset Name / Tag | Asset Type | Purdue Level | Zone | Known CVEs? | Highest CVSS Score | Patch / Support Status | Auth & Encryption? | Remote Access? | Vuln Score (1–5) | Process / Function | Safety System (SIL)? | Consequence if Offline | Manual Override? | Blast Radius | Consequence Score (1–5) | Network Segmented? | IT/OT Bridge? | 3rd Party Access? | Physical Access Control | Exposure Score (1–5) | Composite Risk Score | Priority Tier | Recommended Action | Owner / Responsible | Target Date | Status
ICS-001 | PLC-UNIT-01 | PLC | 1 | OT Zone 1 | Yes | 7.8 | EOL | No | No | 4 | Controls conveyor line 3 | No | Line 3 stops. No manual override. | No | Low | 3 | Partial | No | No | Controlled | 3 | 36 | 🟠 High | Replace with Siemens S7-1500. Interim: isolate VLAN, add compensating firewall rules. | OT Engineer | 2025-06-30 | Planned
ICS-002 | PLC-UNIT-02 | PLC | 1 | OT Zone 1 | No | N/A | Active | Yes | No | 1 | Controls assembly robot cell | No | Cell pauses. Manual override available. | Yes | Low | 2 | Yes | No | No | Controlled | 1 | 2 | 🟢 Low | Monitor. Schedule firmware review 2025. No immediate action required. | OT Engineer | 2025-12-31 | Monitoring
ICS-003 | RTU-REMOTE-01 | RTU | 1 | OT Zone 2 | Yes | 8.1 | Extended | No | Yes | 4 | Remote monitoring substation | No | Loss of substation visibility. | No | Medium | 3 | Partial | No | Yes | Uncontrolled | 5 | 60 | 🟠 High | Patch CVE immediately. Decommission undocumented 4G modem. Add MFA for all remote access. | OT Lead + Security | 2025-03-31 | In Progress
ICS-004 | HMI-CTRL-01 | HMI | 2 | OT Zone 1 | Yes | 9.1 | EOL | No | No | 5 | Operator interface for line 3 | No | Operators lose visibility of line 3. | No | Medium | 3 | No | No | No | Controlled | 3 | 45 | 🟠 High | Replace HMI urgently. Running Win7 — no patches since 2020. Interim: physical access only. | OT Engineer | 2025-04-30 | Planned
ICS-005 | EWS-ENG-01 | Engineering WS | 2 | IT/OT DMZ | No | N/A | Active | Partial | Yes | 2 | PLC programming workstation | No | Engineering changes cannot be deployed. | N/A | High | 3 | Partial | Yes | No | Controlled | 4 | 24 | 🟡 Medium | Enforce MFA on RDP. Restrict access by IP. Enable full audit logging. | IT Security | 2025-05-31 | Not Started
ICS-006 | DCS-NODE-01 | DCS Controller | 1 | OT Zone 3 | No | N/A | Active | Partial | No | 2 | Reactor temperature control | Yes — SIL 2 | Safety shutdown triggers if lost. | Yes | High | 5 | Yes | No | No | Controlled | 2 | 20 | 🟡 Medium | SIL 2 loop — all changes require MOC process. Coordinate with safety team before any work. | Safety Engineer | 2025-09-30 | Monitoring
ICS-007 | HIST-01 | Historian Server | 3 | IT/OT DMZ | Yes | 7.2 | Extended | No | No | 3 | Process data historian | No | Loss of historical data logging. | N/A | High | 2 | No | Yes | No | Controlled | 4 | 24 | 🟡 Medium | Patch CVE-2023-31409 urgently. Audit firewall rules. Historian is primary IT/OT bridge. | IT Security + OT | 2025-04-30 | Not Started
ICS-010 | MODEM-4G-UNKN | 4G Modem | 1 | OT Zone 2 | Unknown | Unknown | UNDOCUMENTED | No | Yes | 5 | Unknown — undocumented device | Unknown | Unknown — assess immediately. | No | Unknown | 5 | No | Yes | Yes | None | 5 | 125 | 🔴 Critical | PHYSICALLY DISCONNECT IMMEDIATELY. Investigate vendor access. Document all findings. Do not reconnect until fully assessed. | OT Lead + Management | IMMEDIATE | Urgent

## 🗺️ Zone Map
🗺️ Security Zone Map & Conduit Register ¦ Phase 1 ¦ IEC 62443 Zone & Conduit Model ¦ [MtU #02]
Zone ID | Zone Name | Purdue Level(s) | Assets in Zone | Asset Count | Zone Risk Level | Connected Zones | Conduit / Path | Conduit Encrypted? | Conduit Authenticated? | Firewall / Control? | Key Risk Notes
Z-01 | OT Zone 1 | 0,1,2 | ICS-001, ICS-002, ICS-004 | 3 | 🟠 High | OT Zone 2, IT/OT DMZ | PROFIBUS / EtherNet/IP | No | No | Partial | EOL PLC and HMI present. No encryption on PROFIBUS. HMI running Win7. Priority remediation zone.
Z-02 | OT Zone 2 | 0,1 | ICS-003, ICS-010 | 2 | 🔴 Critical | OT Zone 1, External (undocumented) | DNP3 / Modbus RTU / Cellular | No | No | None | Undocumented 4G modem creates uncontrolled external conduit. Disconnect immediately. Highest risk zone.
Z-03 | OT Zone 3 | 0,1 | ICS-006, ICS-008 | 2 | 🟡 Medium | IT/OT DMZ | HART / OPC-DA | No | No | Yes | SIL 2 DCS loop. All changes require MOC. Currently well-segmented but OPC-DA is unencrypted.
Z-04 | IT/OT DMZ | 2,3 | ICS-005, ICS-007, ICS-009 | 3 | 🟠 High | OT Zone 1, OT Zone 3, Corporate IT | OPC-DA / EtherNet/IP / RDP | Partial | Partial | Yes | Primary IT/OT bridge. Historian and EWS both present. Lateral movement risk. Firewall present but rules unreviewed.
Z-05 | Safety Zone | 1 | Safety systems (separate SIS) | 0 | 🟡 Medium | OT Zone 3 (limited) | Hardwired / limited digital | N/A | N/A | Physical only | SIS independent of main OT network. Physical isolation maintained. Periodic review required.

## 🏆 Priority Shortlist
🏆 Prioritised Migration Shortlist ¦ Phase 1 Output ¦ [MtU #02]
Rank | Asset ID | Asset Name | Zone | Composite Score | Priority Tier | Key Risk Reason | Recommended Action | Owner | Target Date | Status
1 | ICS-010 | MODEM-4G-UNKN | OT Zone 2 | 125 | 🔴 Critical | Undocumented external access. Max score across all dimensions. | PHYSICALLY DISCONNECT IMMEDIATELY. Full investigation required. | OT Lead + Management | IMMEDIATE | Urgent
2 | ICS-004 | HMI-CTRL-01 | OT Zone 1 | 45 | 🟠 High | EOL + Win7 + CVE-2021-37185. No patches since 2020. | Replace HMI. Interim: physical access only, isolate from network. | OT Engineer | 2025-04-30 | Planned
3 | ICS-003 | RTU-REMOTE-01 | OT Zone 2 | 60 | 🟠 High | CVE-2022-37300 + undocumented 4G connection + no authentication. | Patch CVE. Decommission modem. Enforce MFA. Review remote access policy. | OT Lead + Security | 2025-03-31 | In Progress
4 | ICS-001 | PLC-UNIT-01 | OT Zone 1 | 36 | 🟠 High | S7-300 EOL Dec 2024. CVE present. No manual override on controlled process. | Plan S7-1500 replacement. Interim: VLAN isolation + compensating firewall rules. | OT Engineer | 2025-06-30 | Planned
5 | ICS-007 | HIST-01 | IT/OT DMZ | 24 | 🟡 Medium | IT/OT bridge. CVE-2023-31409 unpatched. OPC-DA unencrypted. | Patch CVE urgently. Full firewall ruleset audit. Consider OPC-UA migration. | IT Security + OT | 2025-04-30 | Not Started
6 | ICS-005 | EWS-ENG-01 | IT/OT DMZ | 24 | 🟡 Medium | RDP to PLCs without MFA. High blast radius if compromised. | Enforce MFA. IP restriction on RDP. Enable full audit logging. | IT Security | 2025-05-31 | Not Started
7 | ICS-006 | DCS-NODE-01 | OT Zone 3 | 20 | 🟡 Medium | SIL 2 — consequence score elevated. OPC-DA unencrypted on conduit. | MOC process for all changes. Plan OPC-DA to OPC-UA migration in next maintenance. | Safety Engineer | 2025-09-30 | Monitoring
8 | ICS-009 | FIREWALL-OT-01 | IT/OT DMZ | 15 | 🟡 Medium | Firewall rules unreviewed 12+ months. IDS signatures outdated. | Full ruleset audit. Update IDS. Establish quarterly review cadence. | IT Security | 2025-04-30 | Not Started
9 | ICS-002 | PLC-UNIT-02 | OT Zone 1 | 2 | 🟢 Low | Active support, no CVEs, manual override available. | Monitor. Firmware review Q4 2025. No urgent action required. | OT Engineer | 2025-12-31 | Monitoring

## 📖 Reference
📖 Reference Guide ¦ Scoring Rubrics, Consequence Scale & Standards
VULNERABILITY SCORE RUBRIC (1–5)
| Score 5 — Critical | EOL device with known high-severity CVEs (CVSS 7+), no authentication, no encryption, internet-facing or with remote access.
| Score 4 — High | EOL or extended support with CVEs, limited authentication, some network exposure.
| Score 3 — Medium | Extended support or active with known CVEs, partial authentication, limited exposure.
| Score 2 — Low | Active support, no known CVEs, some authentication gaps, well-segmented network.
| Score 1 — Minimal | Active support, no known CVEs, full authentication and encryption, no remote access.
CONSEQUENCE SCORE RUBRIC (1–5)
| Score 5 — Catastrophic | Loss of life, major environmental incident, total facility shutdown, SIL 2+ safety system impact.
| Score 4 — Critical | Serious injury risk, major production loss, significant safety system dependency, no redundancy.
| Score 3 — Major | Minor injury possible, significant downtime, partial production loss, limited manual override.
| Score 2 — Moderate | No injury risk, limited downtime, contained impact, manual override available.
| Score 1 — Minor | No safety impact, minimal operational impact, full redundancy and manual override in place.
EXPOSURE SCORE RUBRIC (1–5)
| Score 5 — Critical | No network segmentation, external internet access or undocumented remote paths, no physical access control.
| Score 4 — High | Partial segmentation, IT/OT bridge device, third-party remote access without strong controls.
| Score 3 — Medium | Segmented but firewall rules unreviewed, some remote access with basic controls.
| Score 2 — Low | Well-segmented, no remote access, controlled physical access, firewall actively managed.
| Score 1 — Minimal | Air-gapped or fully isolated, no remote access, strict physical access control enforced.
COMPOSITE SCORE & PRIORITY TIERS
| Formula | Composite Score = Vulnerability Score × Consequence Score × Exposure Score (range: 1–125)
| 🔴 Critical (75–125) | Immediate action within 30 days. Escalate to management. Document interim compensating controls.
| 🟠 High (40–74) | Action within 90 days. Schedule into next maintenance window. Assign owner and target date.
| 🟡 Medium (15–39) | Action within 6 months. Include in next project planning cycle. Monitor in interim.
| 🟢 Low (1–14) | Annual review. No immediate action required. Maintain current controls and monitoring.
KEY STANDARDS
| IEC 62443 | Primary international standard for OT/ICS security. Zone and conduit model from IEC 62443-3-3. Security levels SL1–SL4 define target security posture.
| IEC 61508 / 61511 | Functional safety standards defining Safety Integrity Levels (SIL 1–4). Any SIS device must be assessed under this framework.
| NIST SP 800-82 | US guide to OT security. Practical companion to IEC 62443. Freely available at nist.gov/publications.
| EU CRA (Dec 2027) | Cyber Resilience Act. Drives manufacturer compliance. Indirect pressure on asset owners via insurance and procurement.
| EU NIS2 | Already in force. Applies to operators of essential services. Requires demonstrable OT risk management now.
| CVE / CVSS | Search cve.mitre.org for any device model and firmware. CVSS score guides vulnerability severity input to this matrix.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #02] ¦ Template v1.0 ¦ Cite freely with attribution