## 📋 Cover
🏭 ICS Asset Inventory Migrating the Unmigrateable — Study Notes ¦ [MtU #01]
Phase 0 — Asset Discovery Template ¦ IEC 62443 & CRA Aligned
PROJECT INFORMATION
Facility / Site Name
Assessment Lead
Organisation
Date Started
Date Last Updated
Assessment Version | v1.0
Classification | CONFIDENTIAL
HOW TO USE THIS TEMPLATE
📄 Asset Inventory | Complete one row per ICS device discovered on site. Use passive monitoring + manual walkdown.
🌐 Network Topology | Document network zones, connections and unexpected access paths.
⚠️ Risk Flags | Auto-highlights EOL, unsupported and high-CVE devices requiring priority attention.
📖 Reference | Definitions, scoring guidance and CRA/IEC 62443 reference notes.
⚡ Part of the 'Migrating the Unmigrateable' series ¦ linkedin.com

## 📊 Asset Inventory
🏭 ICS Asset Inventory ¦ Phase 0 — Asset Discovery ¦ Migrating the Unmigrateable [MtU #01]
Asset ID | Asset Name / Tag | Asset Type | Manufacturer | Model / Part No. | Firmware / SW Version | Serial Number | Purdue Level | Physical Location | Network Zone | IP Address | MAC Address | Protocol(s) | Connected To (Asset ID) | Remote Access? | Install Year | Expected EOL Date | Vendor Support Status | Last Maintenance Date | Known CVEs? | CVE Reference(s) | Process / Function | Consequence if Offline | Manual Override? | Priority Flag | Notes / Comments
ICS-001 | PLC-UNIT-01 | PLC | Siemens | S7-300 | V3.3.17 | SN-2009-001 | 1 | Production Hall A | OT Zone 1 | 192.168.10.10 | AA:BB:CC:DD:EE:01 | PROFIBUS / MPI | ICS-004, ICS-005 | No | 2009 | 2024-12-31 | EOL | 2022-03-15 | Yes | CVE-2019-13945 | Controls conveyor line 3 | Line 3 stops. No manual override. | No | 🔴 Critical | Firmware no longer patched. Priority replacement.
ICS-002 | PLC-UNIT-02 | PLC | Rockwell | ControlLogix L71 | V30.014 | SN-2018-002 | 1 | Production Hall B | OT Zone 1 | 192.168.10.11 | AA:BB:CC:DD:EE:02 | EtherNet/IP | ICS-006 | No | 2018 | 2030-06-30 | Active | 2024-01-20 | No |  | Controls assembly robot cell | Cell pauses. Manual override available. | Yes | 🟢 Low | Well maintained. Schedule firmware review 2025.
ICS-003 | RTU-REMOTE-01 | RTU | Schneider | Sepam T40 | V02.06 | SN-2012-003 | 1 | Substation East | OT Zone 2 | 192.168.20.5 | AA:BB:CC:DD:EE:03 | DNP3 / Modbus RTU | ICS-007 | Yes | 2012 | 2026-03-31 | Extended Support | 2023-06-01 | Yes | CVE-2022-37300 | Remote monitoring substation | Loss of substation visibility. | No | 🟠 High | Remote access via 4G modem — UNDOCUMENTED until this assessment.
ICS-004 | HMI-CTRL-01 | HMI | Siemens | WinCC v7.2 | V7.2 SP2 | SN-2011-004 | 2 | Control Room | OT Zone 1 | 192.168.10.50 | AA:BB:CC:DD:EE:04 | PROFINET | ICS-001 | No | 2011 | 2023-12-31 | EOL | 2021-09-10 | Yes | CVE-2021-37185 | Operator interface for line 3 | Operators lose visibility of line 3. | No | 🔴 Critical | Running Windows 7 embedded. No patches since 2020.
ICS-005 | EWS-ENG-01 | Engineering WS | Dell | OptiPlex 7050 | Win10 LTSC | SN-2019-005 | 2 | Engineering Office | IT/OT DMZ | 192.168.30.10 | AA:BB:CC:DD:EE:05 | EtherNet/IP / RDP | ICS-001, ICS-002 | Yes | 2019 | 2027-10-31 | Active | 2024-02-28 | No |  | PLC programming workstation | Engineering changes cannot be deployed. | N/A | 🟡 Medium | RDP enabled. Ensure MFA is enforced.
ICS-006 | DCS-NODE-01 | DCS Controller | Honeywell | Experion PKS C300 | R501.2 | SN-2015-006 | 1 | Process Area C | OT Zone 3 | 192.168.40.10 | AA:BB:CC:DD:EE:06 | HART / OPC-DA | ICS-008 | No | 2015 | 2028-12-31 | Active | 2023-11-15 | No |  | DCS node for reactor temperature | Reactor temp control lost. Safety shutdown triggers. | Yes | 🟡 Medium | SIL 2 loop. Coordinate any changes with safety team.
ICS-007 | HIST-01 | Historian Server | OSIsoft | PI Server 2016 | 3.4.390 | SN-2016-007 | 3 | Server Room | IT/OT DMZ | 192.168.30.20 | AA:BB:CC:DD:EE:07 | OPC-DA / PI | ICS-003, ICS-006 | No | 2016 | 2026-06-30 | Extended Support | 2023-04-12 | Yes | CVE-2023-31409 | Process data historian | Loss of historical data logging. | N/A | 🟠 High | Bridges OT and IT networks. Key attack surface. Patch urgently.
ICS-008 | SENSOR-TMP-01 | Temperature Sensor | Endress+Hauser | iTEMP TMT142 | FW 01.04 | SN-2014-008 | 0 | Reactor Vessel R-1 | Field | N/A (Serial) | N/A | HART | ICS-006 | No | 2014 | 2029-12-31 | Active | 2024-01-05 | No |  | Reactor inlet temperature | Incorrect temp reading — potential overheat. | No | 🟢 Low | Calibration due Q3 2024.
ICS-009 | FIREWALL-OT-01 | Firewall | Fortinet | FortiGate 100F | 7.2.5 | SN-2022-009 | 2 | Network Cabinet A | IT/OT DMZ | 192.168.30.1 | AA:BB:CC:DD:EE:09 | TCP/IP | All zones | No | 2022 | 2029-12-31 | Active | 2024-03-01 | No |  | IT/OT network segmentation | Loss of network boundary between IT and OT. | N/A | 🟡 Medium | Ruleset review overdue. No IDS signature update since Jan 2024.
ICS-010 | MODEM-4G-UNKN | 4G Modem | Sierra Wireless | RV55 | Unknown | Unknown | 1 | Substation East | OT Zone 2 | DHCP/Dynamic | Unknown | Cellular / PPP | ICS-003 | Yes | Unknown | Unknown | ⚠️ UNDOCUMENTED | Unknown | Unknown |  | Unknown — discovered during walkdown | Unknown — assess immediately. | No | 🔴 Critical | NOT IN ANY PRIOR DOCUMENTATION. Vendor access point? Investigate immediately.

## 🌐 Network Topology
🌐 Network Topology & Connection Register ¦ Phase 0 — Asset Discovery ¦ [MtU #01]
Connection ID | Source Asset ID | Source Asset Name | Source Zone | Destination Asset ID | Destination Name | Destination Zone | Protocol | Port(s) | Direction | Encrypted? | Authenticated? | Connection Type | Business Justified? | Risk Note
CON-001 | ICS-001 | PLC-UNIT-01 | OT Zone 1 | ICS-004 | HMI-CTRL-01 | OT Zone 1 | PROFIBUS | N/A | Bidirectional | No | No | Operational | Yes | Legacy protocol. No auth or encryption. Physical network isolation is only control.
CON-002 | ICS-002 | PLC-UNIT-02 | OT Zone 1 | ICS-005 | EWS-ENG-01 | IT/OT DMZ | EtherNet/IP | 44818 | Bidirectional | No | No | Operational | Yes | Engineering access to PLC. RDP also enabled on EWS. Enforce MFA.
CON-003 | ICS-003 | RTU-REMOTE-01 | OT Zone 2 | ICS-010 | MODEM-4G-UNKN | OT Zone 2 | PPP/Cellular | Dynamic | Outbound | No | No | ⚠️ UNDOCUMENTED | No | CRITICAL: Undocumented remote path. Unknown who has access. Isolate immediately.
CON-004 | ICS-007 | HIST-01 | IT/OT DMZ | ICS-006 | DCS-NODE-01 | OT Zone 3 | OPC-DA | 135 | Bidirectional | No | No | Operational | Yes | OPC-DA is unencrypted. Historian bridges IT and OT — high value target.
CON-005 | ICS-009 | FIREWALL-OT-01 | IT/OT DMZ | All | All OT Zones | OT Zones | TCP/IP | Various | Bidirectional | Yes | Yes | Security | Yes | Firewall rules require full audit. Last review unknown.
CON-006 | ICS-005 | EWS-ENG-01 | IT/OT DMZ | ICS-001 | PLC-UNIT-01 | OT Zone 1 | MPI/PROFIBUS | N/A | Bidirectional | No | No | Operational | Yes | Direct programming connection. No change management controls observed.

## ⚠️ Risk Flags
⚠️ Risk Flags Summary ¦ Phase 0 Output ¦ Migrating the Unmigrateable [MtU #01]
ℹ️ This sheet summarises the highest priority findings from Asset Inventory. Update manually after each assessment cycle.
Asset ID | Asset Name | Risk Category | Finding | Priority | Recommended Action
ICS-001 | PLC-UNIT-01 | End of Life | Siemens S7-300 EOL Dec 2024. No security patches available. | 🔴 Critical | Plan replacement with S7-1500 series. Interim: network isolation + compensating controls.
ICS-004 | HMI-CTRL-01 | End of Life + OS | WinCC v7.2 EOL. Running Windows 7 Embedded with no patches since 2020. | 🔴 Critical | Replace HMI. Interim: isolate from all networks, restrict physical access.
ICS-010 | MODEM-4G-UNKN | Undocumented Access | 4G modem found during walkdown. Not in any documentation. Unknown access parties. | 🔴 Critical | Physically disconnect immediately. Investigate vendor access. Document findings.
ICS-003 | RTU-REMOTE-01 | Known CVE | CVE-2022-37300 identified. Remote code execution risk on Schneider Sepam T40. | 🟠 High | Apply vendor patch. Review remote access via undocumented modem (CON-003).
ICS-007 | HIST-01 | IT/OT Bridge + CVE | Historian bridges IT and OT zones. CVE-2023-31409 unpatched. High lateral movement risk. | 🟠 High | Patch immediately. Audit firewall rules between historian and OT zones.
ICS-005 | EWS-ENG-01 | Remote Access Risk | RDP enabled on engineering workstation with direct PLC access. MFA not enforced. | 🟡 Medium | Enforce MFA on all remote access. Restrict RDP to specific IPs. Enable logging.
ICS-009 | FIREWALL-OT-01 | Config Drift | Firewall ruleset not reviewed in 12+ months. IDS signatures outdated. | 🟡 Medium | Conduct full ruleset audit. Update IDS signatures. Establish review cadence.

## 📖 Reference
📖 Reference Guide ¦ Definitions, Standards & Scoring Guidance
PURDUE MODEL LEVELS
Level 0 | Field Devices — Sensors, actuators, drives, valves directly interfacing with physical process.
Level 1 | Basic Control — PLCs, RTUs, DCS controllers executing control logic.
Level 2 | Supervisory Control — SCADA systems, HMIs, engineering workstations.
Level 3 | Site Operations — Historians, site-level business systems, data aggregation.
Level 4 | Enterprise — IT systems, ERP, corporate network. Outside OT scope.
VENDOR SUPPORT STATUS
Active | Manufacturer provides full security patches, updates and technical support.
Extended Support | Limited support. Security patches may be available but functionality updates ceased.
EOL | End of Life. No patches, no support. Compensating controls mandatory.
UNDOCUMENTED | Device found during assessment with no prior documentation. Treat as critical risk until investigated.
PRIORITY FLAG GUIDANCE
🔴 Critical | Immediate action required. EOL device with known CVEs, undocumented access, or critical process with no redundancy.
🟠 High | Action required within 90 days. Known vulnerability, extended support expiring, or inadequate network segmentation.
🟡 Medium | Action required within 6 months. Configuration gaps, overdue maintenance, or access control weaknesses.
🟢 Low | Monitor. No known vulnerabilities, active support, appropriate controls in place. Schedule routine review.
KEY STANDARDS REFERENCE
IEC 62443 | International standard for Industrial Automation and Control System security. The primary framework for OT security. Series covers policies, procedures, system and component requirements.
NIST SP 800-82 | US NIST Guide to OT Security. Excellent practical companion to IEC 62443. Freely available at nist.gov.
EU CRA | Cyber Resilience Act. Applies to manufacturers of products with digital elements sold in EU market from Dec 2027. Drives OEM compliance but creates indirect pressure on asset owners.
EU NIS2 | Network and Information Security Directive 2. Already in force. Applies to operators of essential services. Requires OT risk management NOW, not 2027.
CVE Database | cve.mitre.org — search any device model/firmware to identify known vulnerabilities. Essential during Phase 0.
⚡ Migrating the Unmigrateable — Study Notes ¦ [MtU #01] ¦ Template v1.0 ¦ Cite freely with attribution